## Sheet1
No | NAME | Address Byte_OPC NODE | Address Bit | DataType | Tag Description | PLC | McSIM | Data Concept | Object Concept | H2M | H2M PID | IP1 | IP1 PID
1 | D1_Authorisation | 0 | 0 | BOOL | Zone D1 Available | BPCS/PSD | NO | Status | HRS | YES | NA | YES | NA
2 | D2_Authorisation | 0 | 1 | BOOL | Zone D2 Available | BPCS/PSD | NO | Status | HRS | NO | NA | YES | NA
3 | D3_Authorisation | 0 | 2 | BOOL | Zone D3 Available | BPCS/PSD | NO | Status | HRS | NO | NA | NO | NA
4 | D4_Authorisation | 0 | 3 | BOOL | Zone D4 Available | BPCS/PSD | NO | Status | HRS | NO | NA | NO | NA
5 | Common_Authorisation | 0 | 4 | BOOL | Zone Common Available | BPCS/PSD | NO | Status | HRS | YES | NA | YES | NA
6 | Comp_Authorisation | 0 | 5 | BOOL | Zone Compression Available | BPCS/PSD | NO | Status | HRS | YES | NA | YES | NA
7 | GEMMA_Mode_Utilities | 0 | 6 | BOOL | HRS MODE Utilities, 1 = Activated 0= Deactivated | BPCS/PSD | NO | Status | GEMMA | YES | NA | YES | NA
8 | GEMMA_Mode_Stop | 0 | 7 | BOOL | HRS MODE STOP, 1 = Activated 0= Deactivated | BPCS/PSD | NO | Status | GEMMA | YES | NA | YES | NA
9 | GEMMA_Mode_Offline | 1 | 0 | BOOL | HRS MODE Offlinel, 1 = Activated 0= Deactivated | BPCS/PSD | NO | Status | GEMMA | YES | NA | YES | NA
10 | GEMMA_Mode_Normal | 1 | 1 | BOOL | HRS MODE Normal, 1 = Activated 0= Deactivated | BPCS/PSD | NO | Status | GEMMA | YES | NA | YES | NA
11 | GEMMA_Mode_Maint | 1 | 2 | BOOL | HRS MODE Maint, 1 = Activated 0= Deactivated | BPCS/PSD | NO | Status | GEMMA | YES | NA | YES | NA
12 | GEMMA_Mode_Degrade | 1 | 3 | BOOL | HRS MODE Degrade, 1 = Activated 0= Deactivated | BPCS/PSD | NO | Status | GEMMA | YES | NA | YES | NA
13 | GEMMA_CMD_HRStoMaint | 1 | 4 | BOOL | Button Active Mode Maintenance | BPCS/PSD | NO | CMD | GEMMA | YES | NA | YES | NA
14 | GEMMA_CMD_HRStoMarche | 1 | 5 | BOOL | Button Active Mode Start | BPCS/PSD | NO | CMD | GEMMA | YES | NA | YES | NA
15 | GEMMA_CMD_HRStoStop | 1 | 6 | BOOL | Button Active Mode Stop | BPCS/PSD | NO | CMD | GEMMA | YES | NA | YES | NA
16 | GEMMA_CMD_MaintSecuOK | 4722 | 4 | BOOL | Button maintenance effectuée | BPCS/PSD | NO | CMD | GEMMA | YES | NA | YES | NA
17 | API_Version | 2 | 0 | REAL | Versioning Automate BPCS PSD | BPCS/PSD | NO | Versioning | HRS | YES | NA | YES | NA
18 | HMI_Version | 6 | 0 | REAL | Versioning HMI Maintenance | BPCS/PSD | NO | Versioning | HRS | YES | NA | YES | NA
19 | MES_PT_Air_Comp | 10 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | YES | PT 12.1 | YES | PT 12.1
20 | ScaleMIN_PT_Air_Comp | 14 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | PT | YES | PT 12.1 | YES | PT 12.1
21 | ScaleMAX_PT_Air_Comp | 18 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | PT | YES | PT 12.1 | YES | PT 12.1
22 | ModeSimu_PT_Air_Comp | 22 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | YES | PT 12.1 | YES | PT 12.1
23 | CMDSimu_PT_Air_Comp | 24 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | YES | PT 12.1 | YES | PT 12.1
24 | ActPSDSL_PT_Air_Comp | 28 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | YES | PT 12.1 | YES | PT 12.1
25 | PSDSL_PT_Air_Comp | 30 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | YES | PT 12.1 | YES | PT 12.1
26 | ActPSDSH_PT_Air_Comp | 34 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | YES | PT 12.1 | YES | PT 12.1
27 | PSDSH_PT_Air_Comp | 36 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | YES | PT 12.1 | YES | PT 12.1
28 | Type_PT_Air_Comp | 40 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | YES | PT 12.1 | YES | PT 12.1
29 | Hysteresis_Air_Comp | 3798 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | YES | PT 12.1 | YES | PT 12.1
30 | Offset_Air_Comp | 3802 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | YES | PT 12.1 | YES | PT 12.1
31 | Channel_Def_Air_Comp | 4179 | 2 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | YES | PT 12.1 | YES | PT 12.1
32 | MES_PT_STK1 | 42 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
33 | ScaleMIN_PT_STK1 | 46 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
34 | ScaleMAX_PT_STK1 | 50 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
35 | ModeSimu_PT_STK1 | 54 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
36 | CMDSimu_PT_STK1 | 56 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
37 | ActPSDSL_PT_STK1 | 60 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
38 | PSDSL_PT_STK1 | 62 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
39 | ActPSDSH_PT_STK1 | 66 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
40 | PSDSH_PT_STK1 | 68 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
41 | Type_PT_STK1 | 72 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
42 | Hysteresis_PT_STK1 | 3806 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
43 | Offset_PT_STK1 | 3810 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
44 | Channel_Def_PT_STK1 | 4179 | 3 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
45 | MES_PT_STK2 | 74 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
46 | ScaleMIN_PT_STK2 | 78 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
47 | ScaleMAX_PT_STK2 | 82 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
48 | ModeSimu_PT_STK2 | 86 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
49 | CMDSimu_PT_STK2 | 88 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
50 | ActPSDSL_PT_STK2 | 92 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
51 | PSDSL_PT_STK2 | 94 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
52 | ActPSDSH_PT_STK2 | 98 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
53 | PSDSH_PT_STK2 | 100 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
54 | Type_PT_STK2 | 104 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
55 | Hysteresis_PT_STK2 | 3814 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
56 | Offset_PT_STK2 | 3818 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
57 | Channel_Def_PT_STK2 | 4179 | 4 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
58 | MES_PT_STK3 | 106 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
59 | ScaleMIN_PT_STK3 | 110 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
60 | ScaleMAX_PT_STK3 | 114 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
61 | ModeSimu_PT_STK3 | 118 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
62 | CMDSimu_PT_STK3 | 120 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
63 | ActPSDSL_PT_STK3 | 124 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
64 | PSDSL_PT_STK3 | 126 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
65 | ActPSDSH_PT_STK3 | 130 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
66 | PSDSH_PT_STK3 | 132 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
67 | Type_PT_STK3 | 136 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
68 | Hysteresis_PT_STK3 | 3822 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
69 | Offset_PT_STK3 | 3826 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
70 | Channel_Def_PT_STK3 | 4179 | 5 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
71 | MES_PT_STK4 | 138 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
72 | ScaleMIN_PT_STK4 | 142 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
73 | ScaleMAX_PT_STK4 | 146 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
74 | ModeSimu_PT_STK4 | 150 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
75 | CMDSimu_PT_STK4 | 152 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
76 | ActPSDSL_PT_STK4 | 156 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
77 | PSDSL_PT_STK4 | 158 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
78 | ActPSDSH_PT_STK4 | 162 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
79 | PSDSH_PT_STK4 | 164 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
80 | Type_PT_STK4 | 168 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
81 | Hysteresis_PT_STK4 | 3830 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
82 | Offset_PT_STK4 | 3834 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
83 | Channel_Def_PT_STK4 | 4179 | 6 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
84 | MES_PT_STK5 | 170 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
85 | ScaleMIN_PT_STK5 | 174 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
86 | ScaleMAX_PT_STK5 | 178 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
87 | ModeSimu_PT_STK5 | 182 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
88 | CMDSimu_PT_STK5 | 184 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
89 | ActPSDSL_PT_STK5 | 188 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
90 | PSDSL_PT_STK5 | 190 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
91 | ActPSDSH_PT_STK5 | 194 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
92 | PSDSH_PT_STK5 | 196 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
93 | Type_PT_STK5 | 200 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
94 | Hysteresis_PT_STK5 | 3838 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
95 | Offset_PT_STK5 | 3842 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
96 | Channel_Def_PT_STK5 | 4179 | 7 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
97 | MES_PT_STK6 | 202 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
98 | ScaleMIN_PT_STK6 | 206 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
99 | ScaleMAX_PT_STK6 | 210 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
100 | ModeSimu_PT_STK6 | 214 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
101 | CMDSimu_PT_STK6 | 216 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
102 | ActPSDSL_PT_STK6 | 220 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
103 | PSDSL_PT_STK6 | 222 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
104 | ActPSDSH_PT_STK6 | 226 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
105 | PSDSH_PT_STK6 | 228 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
106 | Type_PT_STK6 | 232 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
107 | Hysteresis_PT_STK6 | 3846 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
108 | Offset_PT_STK6 | 3850 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
109 | Channel_Def_PT_STK6 | 4180 | 0 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
110 | MES_PT_STK7 | 234 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
111 | ScaleMIN_PT_STK7 | 238 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
112 | ScaleMAX_PT_STK7 | 242 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
113 | ModeSimu_PT_STK7 | 246 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
114 | CMDSimu_PT_STK7 | 248 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
115 | ActPSDSL_PT_STK7 | 252 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
116 | PSDSL_PT_STK7 | 254 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
117 | ActPSDSH_PT_STK7 | 258 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
118 | PSDSH_PT_STK7 | 260 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
119 | Type_PT_STK7 | 264 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
120 | Hysteresis_PT_STK7 | 3854 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
121 | Offset_PT_STK7 | 3858 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
122 | Channel_Def_PT_STK7 | 4180 | 1 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
123 | MES_PT_STK8 | 266 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
124 | ScaleMIN_PT_STK8 | 270 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
125 | ScaleMAX_PT_STK8 | 274 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
126 | ModeSimu_PT_STK8 | 278 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
127 | CMDSimu_PT_STK8 | 280 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
128 | ActPSDSL_PT_STK8 | 284 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
129 | PSDSL_PT_STK8 | 286 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
130 | ActPSDSH_PT_STK8 | 290 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
131 | PSDSH_PT_STK8 | 292 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
132 | Type_PT_STK8 | 296 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
133 | Hysteresis_PT_STK8 | 3862 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
134 | Offset_PT_STK8 | 3866 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
135 | Channel_Def_PT_STK8 | 4180 | 2 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
136 | MES_PT_STK9 | 298 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
137 | ScaleMIN_PT_STK9 | 302 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
138 | ScaleMAX_PT_STK9 | 306 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
139 | ModeSimu_PT_STK9 | 310 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
140 | CMDSimu_PT_STK9 | 312 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
141 | ActPSDSL_PT_STK9 | 316 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
142 | PSDSL_PT_STK9 | 318 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
143 | ActPSDSH_PT_STK9 | 322 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
144 | PSDSH_PT_STK9 | 324 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
145 | Type_PT_STK9 | 328 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
146 | Hysteresis_PT_STK9 | 3870 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
147 | Offset_PT_STK9 | 3874 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
148 | Channel_Def_PT_STK9 | 4180 | 3 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
149 | MES_PT_STK10 | 330 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | YES | PT 1.1 | NO | PT 1.1
150 | ScaleMIN_PT_STK10 | 334 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | PT | YES | PT 1.1 | NO | PT 1.1
151 | ScaleMAX_PT_STK10 | 338 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | PT | YES | PT 1.1 | NO | PT 1.1
152 | ModeSimu_PT_STK10 | 342 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | YES | PT 1.1 | NO | PT 1.1
153 | CMDSimu_PT_STK10 | 344 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | YES | PT 1.1 | NO | PT 1.1
154 | ActPSDSL_PT_STK10 | 348 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | YES | PT 1.1 | YES | PT 1.1
155 | PSDSL_PT_STK10 | 350 | 0 | REAL | PRM Seuil PSD L | BPCS/PSD | NO | PRM | PT | YES | PT 1.1 | YES | PT 1.1
156 | ActPSDSH_PT_STK10 | 354 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | YES | PT 1.1 | YES | PT 1.1
157 | PSDSH_PT_STK10 | 356 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | YES | PT 1.1 | YES | PT 1.1
158 | Type_PT_STK10 | 360 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | YES | PT 1.1 | NO | PT 1.1
159 | Hysteresis_PT_STK10 | 3878 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | YES | PT 1.1 | YES | PT 1.1
160 | Offset_PT_STK10 | 3882 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | YES | PT 1.1 | YES | PT 1.1
161 | Channel_Def_PT_STK10 | 4180 | 4 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | YES | PT 1.1 | NO | PT 1.1
162 | MES_PT_STK11 | 362 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | YES | PT 3.1
163 | ScaleMIN_PT_STK11 | 366 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.1
164 | ScaleMAX_PT_STK11 | 370 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.1
165 | ModeSimu_PT_STK11 | 374 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | YES | PT 3.1
166 | CMDSimu_PT_STK11 | 376 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | YES | PT 3.1
167 | ActPSDSL_PT_STK11 | 380 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.1
168 | PSDSL_PT_STK11 | 382 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.1
169 | ActPSDSH_PT_STK11 | 386 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.1
170 | PSDSH_PT_STK11 | 388 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.1
171 | Type_PT_ST11 | 392 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.1
172 | Hysteresis_PT_STK11 | 3886 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.1
173 | Offset_PT_STK11 | 3890 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.1
174 | Channel_Def_PT_STK11 | 4180 | 5 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | YES | PT 3.1
175 | MES_PT_STK12 | 394 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | YES | PT 3.2
176 | ScaleMIN_PT_STK12 | 398 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.2
177 | ScaleMAX_PT_STK12 | 402 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.2
178 | ModeSimu_PT_STK12 | 406 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | YES | PT 3.2
179 | CMDSimu_PT_STK12 | 408 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | YES | PT 3.2
180 | ActPSDSL_PT_STK12 | 412 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.2
181 | PSDSL_PT_STK12 | 414 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.2
182 | ActPSDSH_PT_STK12 | 418 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.2
183 | PSDSH_PT_STK12 | 420 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.2
184 | Type_PT_STK12 | 424 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.2
185 | Hysteresis_PT_STK12 | 3894 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.2
186 | Offset_PT_STK12 | 3898 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.2
187 | Channel_Def_PT_STK12 | 4180 | 6 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | YES | PT 3.2
188 | MES_PT_STK13 | 426 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | YES | PT 3.3
189 | ScaleMIN_PT_STK13 | 430 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.3
190 | ScaleMAX_PT_STK13 | 434 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.3
191 | ModeSimu_PT_STK13 | 438 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | YES | PT 3.3
192 | CMDSimu_PT_STK13 | 440 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | YES | PT 3.3
193 | ActPSDSL_PT_STK13 | 444 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.3
194 | PSDSL_PT_STK13 | 446 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.3
195 | ActPSDSH_PT_STK13 | 450 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.3
196 | PSDSH_PT_STK13 | 452 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.3
197 | Type_PT_STK13 | 456 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.3
198 | Hysteresis_PT_STK13 | 3902 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.3
199 | Offset_PT_STK13 | 3906 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.3
200 | Channel_Def_PT_STK13 | 4180 | 7 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | YES | PT 3.3
201 | MES_PT_STK14 | 458 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | YES | PT 3.4
202 | ScaleMIN_PT_STK14 | 462 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.4
203 | ScaleMAX_PT_STK14 | 466 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.4
204 | ModeSimu_PT_STK14 | 470 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | YES | PT 3.4
205 | CMDSimu_PT_STK14 | 472 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | YES | PT 3.4
206 | ActPSDSL_PT_STK14 | 476 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.4
207 | PSDSL_PT_STK14 | 478 | 0 | REAL | PRM Seuil PSD L | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.4
208 | ActPSDSH_PT_STK14 | 482 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.4
209 | PSDSH_PT_STK14 | 484 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.4
210 | Type_PT_ST14 | 488 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.4
211 | Hysteresis_PT_STK14 | 3910 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.4
212 | Offset_PT_STK14 | 3914 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 3.4
213 | Channel_Def_PT_STK14 | 4181 | 0 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | YES | PT 3.4
214 | MES_PT_STK15 | 490 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
215 | ScaleMIN_PT_STK15 | 494 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
216 | ScaleMAX_PT_STK15 | 498 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
217 | ModeSimu_PT_STK15 | 502 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
218 | CMDSimu_PT_STK15 | 504 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
219 | ActPSDSL_PT_STK15 | 508 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
220 | PSDSL_PT_STK15 | 510 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
221 | ActPSDSH_PT_STK15 | 514 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
222 | PSDSH_PT_STK15 | 516 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
223 | Type_PT_STK15 | 520 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
224 | Hysteresis_PT_STK15 | 3918 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
225 | Offset_PT_STK15 | 3922 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
226 | Channel_Def_PT_STK15 | 4181 | 1 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
227 | MES_PT_STK16 | 522 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
228 | ScaleMIN_PT_STK16 | 526 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
229 | ScaleMAX_PT_STK16 | 530 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
230 | ModeSimu_PT_STK16 | 534 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
231 | CMDSimu_PT_STK16 | 536 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
232 | ActPSDSL_PT_STK16 | 540 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
233 | PSDSL_PT_STK16 | 542 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
234 | ActPSDSH_PT_STK16 | 546 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
235 | PSDSH_PT_STK16 | 548 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
236 | Type_PT_STK16 | 552 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
237 | Hysteresis_PT_STK16 | 3926 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
238 | Offset_PT_STK16 | 3930 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
239 | Channel_Def_PT_STK16 | 4181 | 2 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
240 | MES_PT_STK17 | 554 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
241 | ScaleMIN_PT_STK17 | 558 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
242 | ScaleMAX_PT_STK17 | 562 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
243 | ModeSimu_PT_STK17 | 566 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
244 | CMDSimu_PT_STK17 | 568 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
245 | ActPSDSL_PT_STK17 | 572 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
246 | PSDSL_PT_STK17 | 574 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
247 | ActPSDSH_PT_STK17 | 578 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
248 | PSDSH_PT_STK17 | 580 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
249 | Type_PT_STK17 | 584 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
250 | Hysteresis_PT_STK17 | 3934 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
251 | Offset_PT_STK17 | 3938 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
252 | Channel_Def_PT_STK17 | 4181 | 3 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
253 | MES_PT_STK18 | 586 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
254 | ScaleMIN_PT_STK18 | 590 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
255 | ScaleMAX_PT_STK18 | 594 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
256 | ModeSimu_PT_STK18 | 598 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
257 | CMDSimu_PT_STK18 | 600 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
258 | ActPSDSL_PT_STK18 | 604 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
259 | PSDSL_PT_STK18 | 606 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
260 | ActPSDSH_PT_STK18 | 610 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
261 | PSDSH_PT_STK18 | 612 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
262 | Type_PT_STK18 | 616 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
263 | Hysteresis_PT_STK18 | 3942 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
264 | Offset_PT_STK18 | 3946 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
265 | Channel_Def_PT_STK18 | 4181 | 4 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
266 | MES_PT_STK19 | 618 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
267 | ScaleMIN_PT_STK19 | 622 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
268 | ScaleMAX_PT_STK19 | 626 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
269 | ModeSimu_PT_STK19 | 630 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
270 | CMDSimu_PT_STK19 | 632 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
271 | ActPSDSL_PT_STK19 | 636 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
272 | PSDSL_PT_STK19 | 638 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
273 | ActPSDSH_PT_STK19 | 642 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
274 | PSDSH_PT_STK19 | 644 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
275 | Type_PT_STK19 | 648 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
276 | Hysteresis_PT_STK19 | 3950 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
277 | Offset_PT_STK19 | 3954 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
278 | Channel_Def_PT_STK19 | 4181 | 5 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
279 | MES_PT_STK20 | 650 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
280 | ScaleMIN_PT_STK20 | 654 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
281 | ScaleMAX_PT_STK20 | 658 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
282 | ModeSimu_PT_STK20 | 662 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
283 | CMDSimu_PT_STK20 | 664 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
284 | ActPSDSL_PT_STK20 | 668 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
285 | PSDSL_PT_STK20 | 670 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
286 | ActPSDSH_PT_STK20 | 674 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
287 | PSDSH_PT_STK20 | 676 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
288 | Type_PT_STK20 | 680 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
289 | Hysteresis_PT_STK20 | 3958 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
290 | Offset_PT_STK20 | 3962 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
291 | Channel_Def_PT_STK20 | 4181 | 6 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
292 | MES_PT_STK21 | 682 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | YES | PT 7.1 | NO | NA
293 | ScaleMIN_PT_STK21 | 686 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | PT | YES | PT 7.1 | NO | NA
294 | ScaleMAX_PT_STK21 | 690 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | PT | YES | PT 7.1 | NO | NA
295 | ModeSimu_PT_STK21 | 694 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | YES | PT 7.1 | NO | NA
296 | CMDSimu_PT_STK21 | 696 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | YES | PT 7.1 | NO | NA
297 | ActPSDSL_PT_STK21 | 700 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | YES | PT 7.1 | NO | NA
298 | PSDSL_PT_STK21 | 702 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | YES | PT 7.1 | NO | NA
299 | ActPSDSH_PT_STK21 | 706 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | YES | PT 7.1 | NO | NA
300 | PSDSH_PT_STK21 | 708 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | YES | PT 7.1 | NO | NA
301 | Type_PT_STK21 | 712 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | YES | PT 7.1 | NO | NA
302 | Hysteresis_PT_STK21 | 3966 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | YES | PT 7.1 | NO | NA
303 | Offset_PT_STK21 | 3970 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | YES | PT 7.1 | NO | NA
304 | Channel_Def_PT_STK21 | 4181 | 7 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | YES | PT 7.1 | NO | NA
305 | MES_PT_STK22 | 714 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | YES | PT 7.2 | NO | NA
306 | ScaleMIN_PT_STK22 | 718 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | PT | YES | PT 7.2 | NO | NA
307 | ScaleMAX_PT_STK22 | 722 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | PT | YES | PT 7.2 | NO | NA
308 | ModeSimu_PT_STK22 | 726 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | YES | PT 7.2 | NO | NA
309 | CMDSimu_PT_STK22 | 728 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | YES | PT 7.2 | NO | NA
310 | ActPSDSL_PT_STK22 | 732 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | YES | PT 7.2 | NO | NA
311 | PSDSL_PT_STK22 | 734 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | YES | PT 7.2 | NO | NA
312 | ActPSDSH_PT_STK22 | 738 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | YES | PT 7.2 | NO | NA
313 | PSDSH_PT_STK22 | 740 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | YES | PT 7.2 | NO | NA
314 | Type_PT_STK22 | 744 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | YES | PT 7.2 | NO | NA
315 | Hysteresis_PT_STK22 | 3974 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | YES | PT 7.2 | NO | NA
316 | Offset_PT_STK22 | 3978 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | YES | PT 7.2 | NO | NA
317 | Channel_Def_PT_STK22 | 4182 | 0 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | YES | PT 7.2 | NO | NA
318 | MES_PT_STK23 | 746 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | YES | PT 7.3 | NO | NA
319 | ScaleMIN_PT_STK23 | 750 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | PT | YES | PT 7.3 | NO | NA
320 | ScaleMAX_PT_STK23 | 754 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | PT | YES | PT 7.3 | NO | NA
321 | ModeSimu_PT_STK23 | 758 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | YES | PT 7.3 | NO | NA
322 | CMDSimu_PT_STK23 | 760 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | YES | PT 7.3 | NO | NA
323 | ActPSDSL_PT_STK23 | 764 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | YES | PT 7.3 | NO | NA
324 | PSDSL_PT_STK23 | 766 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | YES | PT 7.3 | NO | NA
325 | ActPSDSH_PT_STK23 | 770 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | YES | PT 7.3 | NO | NA
326 | PSDSH_PT_STK23 | 772 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | YES | PT 7.3 | NO | NA
327 | Type_PT_STK23 | 776 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | YES | PT 7.3 | NO | NA
328 | Hysteresis_PT_STK23 | 3982 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | YES | PT 7.3 | NO | NA
329 | Offset_PT_STK23 | 3986 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | YES | PT 7.3 | NO | NA
330 | Channel_Def_PT_STK23 | 4182 | 1 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | YES | PT 7.3 | NO | NA
331 | MES_PT_STK24 | 778 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
332 | ScaleMIN_PT_STK24 | 782 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
333 | ScaleMAX_PT_STK24 | 786 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
334 | ModeSimu_PT_STK24 | 790 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
335 | CMDSimu_PT_STK24 | 792 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
336 | ActPSDSL_PT_STK24 | 796 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
337 | PSDSL_PT_STK24 | 798 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
338 | ActPSDSH_PT_STK24 | 802 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
339 | PSDSH_PT_STK24 | 804 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
340 | Type_PT_STK24 | 808 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
341 | Hysteresis_PT_STK24 | 3990 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
342 | Offset_PT_STK24 | 3994 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
343 | Channel_Def_PT_STK24 | 4182 | 2 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
344 | MES_PT_STK25 | 810 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
345 | ScaleMIN_PT_STK25 | 814 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
346 | ScaleMAX_PT_STK25 | 818 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
347 | ModeSimu_PT_STK25 | 822 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
348 | CMDSimu_PT_STK25 | 824 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
349 | ActPSDSL_PT_STK25 | 828 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
350 | PSDSL_PT_STK25 | 830 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
351 | ActPSDSH_PT_STK25 | 834 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
352 | PSDSH_PT_STK25 | 836 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
353 | Type_PT_STK25 | 840 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
354 | Hysteresis_PT_STK25 | 3998 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
355 | Offset_PT_STK25 | 4002 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
356 | Channel_Def_PT_STK25 | 4182 | 3 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
357 | MES_PT_STK26 | 842 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
358 | ScaleMIN_PT_STK26 | 846 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
359 | ScaleMAX_PT_STK26 | 850 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
360 | ModeSimu_PT_STK26 | 854 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
361 | CMDSimu_PT_STK26 | 856 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
362 | ActPSDSL_PT_STK26 | 860 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
363 | PSDSL_PT_STK26 | 862 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
364 | ActPSDSH_PT_STK26 | 866 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
365 | PSDSH_PT_STK26 | 868 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
366 | Type_PT_STK26 | 872 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
367 | Hysteresis_PT_STK26 | 4006 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
368 | Offset_PT_STK26 | 4010 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
369 | Channel_Def_PT_STK26 | 4182 | 4 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
370 | MES_PT_STK27 | 874 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
371 | ScaleMIN_PT_STK27 | 878 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
372 | ScaleMAX_PT_STK27 | 882 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
373 | ModeSimu_PT_STK27 | 886 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
374 | CMDSimu_PT_STK27 | 888 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
375 | ActPSDSL_PT_STK27 | 892 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
376 | PSDSL_PT_STK27 | 894 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
377 | ActPSDSH_PT_STK27 | 898 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
378 | PSDSH_PT_STK27 | 900 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
379 | Type_PT_STK27 | 904 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
380 | Hysteresis_PT_STK27 | 4014 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
381 | Offset_PT_STK27 | 4018 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
382 | Channel_Def_PT_STK27 | 4182 | 5 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
383 | MES_PT_STK28 | 906 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
384 | ScaleMIN_PT_STK28 | 910 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
385 | ScaleMAX_PT_STK28 | 914 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
386 | ModeSimu_PT_STK28 | 918 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
387 | CMDSimu_PT_STK28 | 920 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
388 | ActPSDSL_PT_STK28 | 924 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
389 | PSDSL_PT_STK28 | 926 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
390 | ActPSDSH_PT_STK28 | 930 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
391 | PSDSH_PT_STK28 | 932 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
392 | Type_PT_STK28 | 936 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
393 | Hysteresis_PT_STK28 | 4022 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
394 | Offset_PT_STK28 | 4026 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
395 | Channel_Def_PT_STK28 | 4182 | 6 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
396 | MES_PT_STK29 | 938 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
397 | ScaleMIN_PT_STK29 | 942 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
398 | ScaleMAX_PT_STK29 | 946 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
399 | ModeSimu_PT_STK29 | 950 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
400 | CMDSimu_PT_STK29 | 952 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
401 | ActPSDSL_PT_STK29 | 956 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
402 | PSDSL_PT_STK29 | 958 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
403 | ActPSDSH_PT_STK29 | 962 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
404 | PSDSH_PT_STK29 | 964 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
405 | Type_PT_STK29 | 968 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
406 | Hysteresis_PT_STK29 | 4030 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
407 | Offset_PT_STK29 | 4034 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
408 | Channel_Def_PT_STK29 | 4182 | 7 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
409 | MES_PT_STK30 | 970 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
410 | ScaleMIN_PT_STK30 | 974 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
411 | ScaleMAX_PT_STK30 | 978 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
412 | ModeSimu_PT_STK30 | 982 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
413 | CMDSimu_PT_STK30 | 984 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
414 | ActPSDSL_PT_STK30 | 988 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
415 | PSDSL_PT_STK30 | 990 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
416 | ActPSDSH_PT_STK30 | 994 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
417 | PSDSH_PT_STK30 | 996 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
418 | Type_PT_STK30 | 1000 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
419 | Hysteresis_PT_STK30 | 4038 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
420 | Offset_PT_STK30 | 4042 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
421 | Channel_Def_PT_STK30 | 4183 | 0 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
422 | MES_PT_Nitrogen | 1002 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | YES | PT 30.1
423 | ScaleMIN_PT_Nitrogen | 1006 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 30.1
424 | ScaleMAX_PT_Nitrogen | 1010 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 30.1
425 | ModeSimu_PT_Nitrogen | 1014 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | YES | PT 30.1
426 | CMDSimu_PT_Nitrogen | 1016 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | YES | PT 30.1
427 | ActPSDSL_PT_Nitrogen | 1020 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | PT 30.1
428 | PSDSL_PT_Nitrogen | 1022 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | PT 30.1
429 | ActPSDSH_PT_Nitrogen | 1026 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | PT 30.1
430 | PSDSH_PT_Nitrogen | 1028 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | PT 30.1
431 | Type_PT_Nitrogen | 1032 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 30.1
432 | Hyst_PT_Nitrogen | 4046 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | PT 30.1
433 | Offset_PT_Nitrogen | 4050 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | PT 30.1
434 | Channel_Def_PT_Nit | 4183 | 1 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | YES | PT 30.1
435 | MES_TT_Out_2nd_HEAD_BPCS | 1034 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | TT | NO | NA | YES | TT 2.2
436 | ScaleMIN_TT_Out_2nd_HEAD | 1038 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 2.2
437 | ScaleMAX_TT_Out_2nd_HEAD | 1042 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 2.2
438 | ModeSimu_TT_Out_2nd_HEAD | 1046 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | TT | NO | NA | YES | TT 2.2
439 | CMDSimu_TT_Out_2nd_HEAD | 1048 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | TT | NO | NA | YES | TT 2.2
440 | ActPSDSL_TT_Out_2nd_HEAD | 1052 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 2.2
441 | PSDSL_TT_Out_2nd_HEAD | 1054 | 0 | REAL | PRM Seuil PSD L | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 2.2
442 | ActPSDSH_TT_Out_2nd_HEAD | 1058 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 2.2
443 | PSDSH_TT_Out_2nd_HEAD | 1060 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 2.2
444 | Type_TT_Out_2nd_HEAD | 1064 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 2.2
445 | Hyst_TT_Out_2nd_HEAD | 4054 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 2.2
446 | Offs_TT_Out_2nd_HEAD | 4058 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 2.2
447 | Cha_Def_TT_Out_2nd_HEAD | 4183 | 2 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | YES | TT 2.2
448 | MES_TT_Out_1st_HEAD_BPCS | 1066 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | TT | NO | NA | YES | TT 2.1
449 | ScaleMIN_TT_Out_1st_HEAD | 1070 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 2.1
450 | ScaleMAX_TT_Out_1st_HEAD | 1074 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 2.1
451 | ModeSimu_TT_Out_1st_HEAD | 1078 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | TT | NO | NA | YES | TT 2.1
452 | CMDSimu_TT_Out_1st_HEAD | 1080 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | TT | NO | NA | YES | TT 2.1
453 | ActPSDSL_TT_Out_1st_HEAD | 1084 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 2.1
454 | PSDSL_TT_Out_1st_HEAD | 1086 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 2.1
455 | ActPSDSH_TT_Out_1st_HEAD | 1090 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 2.1
456 | PSDSH_TT_Out_1st_HEAD | 1092 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 2.1
457 | Type_TT_Out_1st_HEAD | 1096 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 2.1
458 | Hyst_TT_Out_1st_HEAD | 4062 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 2.1
459 | Offs_TT_Out_1st_HEAD | 4066 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 2.1
460 | Ch_Def_TT_Out_1st_HEAD | 4183 | 3 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | YES | TT 2.1
461 | MES_TT_Compressor_OIL | 1098 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | TT | NO | NA | YES | TT 23
462 | ScaleMIN_TT_Comp_OIL | 1102 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 23
463 | ScaleMAX_TT_Comp_OIL | 1106 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 23
464 | ModeSimu_TT_Comp_OIL | 1110 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | TT | NO | NA | YES | TT 23
465 | CMDSimu_TT_Comp_OIL | 1112 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | TT | NO | NA | YES | TT 23
466 | ActPSDSL_TT_Comp_OIL | 1116 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 23
467 | PSDSL_TT_Compressor_OIL | 1118 | 0 | REAL | PRM Seuil PSD L | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 23
468 | ActPSDSH_TT_Comp_OIL | 1122 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 23
469 | PSDSH_TT_Compressor_OIL | 1124 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 23
470 | Type_TT_Compressor_OIL | 1128 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 23
471 | Hyst_Compressor_OIL | 4070 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 23
472 | Offset_Comp_OIL | 4074 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 23
473 | Cha_Def_TTComp_OIL | 4183 | 4 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | YES | TT 23
474 | MES_TT_Chiller_H2O | 1130 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | TT | NO | NA | YES | TT 20.1
475 | ScaleMIN_TT_Chiller_H2O | 1134 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 20.1
476 | ScaleMAX_TT_Chiller_H2O | 1138 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 20.1
477 | ModeSimu_TT_Chiller_H2O | 1142 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | TT | NO | NA | YES | TT 20.1
478 | CMDSimu_TT_Chiller_H2O | 1144 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | TT | NO | NA | YES | TT 20.1
479 | ActPSDSL_TT_Chiller_H2O | 1148 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 20.1
480 | PSDSL_TT_Chiller_H2O | 1150 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 20.1
481 | ActPSDSH_TT_Chiller_H2O | 1154 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 20.1
482 | PSDSH_TT_Chiller_H2O | 1156 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 20.1
483 | Type_TT_Chiller_H2O | 1160 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 20.1
484 | Hyst_Chiller_H20 | 4078 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 20.1
485 | Offset_Chiller_H20 | 4082 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | TT | NO | NA | YES | TT 20.1
486 | Cha_Def_TTChillerH20 | 4252 | 2 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | YES | TT 20.1
487 | MES_PT_amont_D1 | 1162 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | YES | PT 8.203 | YES | PT 4.21
488 | ScaleMIN_PT_amont_D1 | 1166 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | PT | YES | PT 8.203 | YES | PT 4.21
489 | ScaleMAX_PT_amont_D1 | 1170 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | PT | YES | PT 8.203 | YES | PT 4.21
490 | ModeSimu_PT_amont_D1 | 1174 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | YES | PT 8.203 | YES | PT 4.21
491 | CMDSimu_PT_amont_D1 | 1176 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | YES | PT 8.203 | YES | PT 4.21
492 | ActPSDSL_PT_amont_D1 | 1180 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | PT 4.21
493 | PSDSL_PT_amont_D1 | 1182 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | PT 4.21
494 | ActPSDSH_PT_amont_D1 | 1186 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | PT 4.21
495 | PSDSH_PT_amont_D1 | 1188 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | PT 4.21
496 | Type_PT_amont_D1 | 1192 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | YES | PT 8.203 | YES | PT 4.21
497 | Hyst_PT_amont_D1 | 4086 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | PT 4.21
498 | Offset_PT_amont_D1 | 4090 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | PT 4.21
499 | Cha_Def_PTAmontD1 | 4252 | 3 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | YES | PT 8.203 | YES | PT 4.21
500 | MES_PT_amont_D2 | 1194 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | YES | PT 4.11
501 | ScaleMIN_PT_amont_D2 | 1198 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 4.11
502 | ScaleMAX_PT_amont_D2 | 1202 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 4.11
503 | ModeSimu_PT_amont_D2 | 1206 | 0 | BOOL | PRM ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | YES | PT 4.11
504 | CMDSimu_PT_amont_D2 | 1208 | 0 | REAL | PRM Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | YES | PT 4.11
505 | ActPSDSL_PT_amont_D2 | 1212 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | PT 4.11
506 | PSDSL_PT_amont_D2 | 1214 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | PT 4.11
507 | ActPSDSH_PT_amont_D2 | 1218 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | PT 4.11
508 | PSDSH_PT_amont_D2 | 1220 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | PT 4.11
509 | Type_PT_amont_D2 | 1224 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 4.11
510 | Hyst_PT_amont_D2 | 4094 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | PT 4.11
511 | Offset_PT_amont_D2 | 4098 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | PT 4.11
512 | Cha_Def_PTAmontD2 | 4252 | 4 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | YES | PT 4.11
513 | MES_PT_amont_D3 | 1226 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
514 | ScaleMIN_PT_amont_D3 | 1230 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
515 | ScaleMAX_PT_amont_D3 | 1234 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
516 | ModeSimu_PT_amont_D3 | 1238 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
517 | CMDSimu_PT_amont_D3 | 1240 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
518 | ActPSDSL_PT_amont_D3 | 1244 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
519 | PSDSL_PT_amont_D3 | 1246 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
520 | ActPSDSH_PT_amont_D3 | 1250 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
521 | PSDSH_PT_amont_D3 | 1252 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
522 | Type_PT_amont_D3 | 1256 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
523 | Hyst_PT_amont_D3 | 4102 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
524 | Offset_PT_amont_D3 | 4106 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
525 | Cha_Def_PTAmontD3 | 4252 | 5 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
526 | MES_PT_amont_D4 | 1258 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
527 | ScaleMIN_PT_amont_D4 | 1262 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
528 | ScaleMAX_PT_amont_D4 | 1266 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
529 | ModeSimu_PT_amont_D4 | 1270 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
530 | CMDSimu_PT_amont_D4 | 1272 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
531 | ActPSDSL_PT_amont_D4 | 1276 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
532 | PSDSL_PT_amont_D4 | 1278 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
533 | ActPSDSH_PT_amont_D4 | 1282 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
534 | PSDSH_PT_amont_D4 | 1284 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
535 | Type_PT_amont_D4 | 1288 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
536 | Hyst_PT_amont_D4 | 4110 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
537 | Offset_PT_amont_D4 | 4114 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
538 | Cha_Def_PTAmontD4 | 4252 | 6 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
539 | MES_PT_aval_D1_BPCS | 1290 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | YES | PT 8.202a | YES | PT 4.201a
540 | ScaleMIN_PT_aval_D1_BPCS | 1294 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | PT | YES | PT 8.202a | YES | PT 4.201a
541 | ScaleMAX_PT_aval_D1_BPCS | 1298 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | PT | YES | PT 8.202a | YES | PT 4.201a
542 | ModeSimu_PT_aval_D1_BPCS | 1302 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | YES | PT 8.202a | YES | PT 4.201a
543 | CMDSimu_PPT_aval_D1_BPCS | 1304 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | YES | PT 8.202a | YES | PT 4.201a
544 | ActPSDSL_PT_aval_D1_BPCS | 1308 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | YES | PT 8.202a | YES | PT 4.201a
545 | PSDSL_PT_aval_D1_BPCS | 1310 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | YES | PT 8.202a | YES | PT 4.201a
546 | ActPSDSH_PT_aval_D1_BPCS | 1314 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | YES | PT 8.202a | YES | PT 4.201a
547 | PSDSH_PT_aval_D1_BPCS | 1316 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | YES | PT 8.202a | YES | PT 4.201a
548 | Type_PT_aval_D1_BPCS | 1320 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | YES | PT 8.202a | YES | PT 4.201a
549 | Hyst_PT_aval_D1 | 4118 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | YES | PT 8.202a | YES | PT 4.201a
550 | Offset_PT_aval_D1 | 4122 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | YES | PT 8.202a | YES | PT 4.201a
551 | Cha_Def_PTAvalD1 | 4252 | 7 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | YES | PT 8.202a | YES | PT 4.201a
552 | MES_PT_aval_D2_BPCS | 1322 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | YES | PT 4.101a
553 | ScaleMIN_PT_aval_D2_BPCS | 1326 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 4.101a
554 | ScaleMAX_PT_aval_D2_BPCS | 1330 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 4.101a
555 | ModeSimu_PT_aval_D2_BPCS | 1334 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | YES | PT 4.101a
556 | CMDSimu_PT_aval_D2_BPCS | 1336 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | YES | PT 4.101a
557 | ActPSDSL_PT_aval_D2_BPCS | 1340 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 4.101a
558 | PSDSL_PT_aval_D2_BPCS | 1342 | 0 | REAL | PRM Seuil PSD L | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 4.101a
559 | ActPSDSH_PT_aval_D2_BPCS | 1346 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 4.101a
560 | PSDSH_PT_aval_D2_BPCS | 1348 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 4.101a
561 | Type_PT_aval_D2_BPCS | 1352 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 4.101a
562 | Hyst_PT_aval_D2 | 4126 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 4.101a
563 | Offset_PT_aval_D2 | 4130 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | YES | PT 4.101a
564 | Cha_Def_PTAvalD2 | 4253 | 0 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | YES | PT 4.101a
565 | MES_PT_aval_D3_BPCS | 1354 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
566 | ScaleMIN_PT_aval_D3_BPCS | 1358 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
567 | ScaleMAX_PT_aval_D3_BPCS | 1362 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
568 | ModeSimu_PT_aval_D3_BPCS | 1366 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
569 | CMDSimu_PT_aval_D3_BPCS | 1368 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
570 | ActPSDSL_PT_aval_D3_BPCS | 1372 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
571 | PSDSL_PT_aval_D3_BPCS | 1374 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
572 | ActPSDSH_PT_aval_D3_BPCS | 1378 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
573 | PSDSH_PT_aval_D3_BPCS | 1380 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
574 | Type_PT_aval_D3_BPCS | 1384 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
575 | Hyst_PT_aval_D3 | 4134 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
576 | Offset_PT_aval_D3 | 4138 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
577 | Cha_Def_PTAvalD3 | 4253 | 1 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
578 | MES_PT_aval_D4_BPCS | 1386 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PT | NO | NA | NO | NA
579 | ScaleMIN_PT_aval_D4_BPCS | 1390 | 0 | REAL | Echelle MIN | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
580 | ScaleMAX_PT_aval_D4_BPCS | 1394 | 0 | REAL | Echelle MAX | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
581 | ModeSimu_PT_aval_D4_BPCS | 1398 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
582 | CMDSimu_PT_aval_D4_BPCS | 1400 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | PT | NO | NA | NO | NA
583 | ActPSDSL_PT_aval_D4_BPCS | 1404 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
584 | PSDSL_PT_aval_D4_BPCS | 1406 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
585 | ActPSDSH_PT_aval_D4_BPCS | 1410 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
586 | PSDSH_PT_aval_D4_BPCS | 1412 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
587 | Type_PT_aval_D4_BPCS | 1416 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
588 | Hyst_PT_aval_D4 | 4142 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
589 | Offset_PT_aval_D4 | 4146 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | PT | NO | NA | NO | NA
590 | Cha_Def_PTAvalD4 | 4253 | 2 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PT | NO | NA | NO | NA
591 | MES_FT_D1 | 1418 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | FT | YES | FT 8.201 | YES | FT 4.201
592 | MassFlowRate_FT_D1 | 1422 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | YES | FT 8.201 | YES | FT 4.201
593 | TotalMassFwd_FT_D1 | 1426 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | YES | FT 8.201 | YES | FT 4.201
594 | TotMassRev_FT_D1 | 1430 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | YES | FT 8.201 | YES | FT 4.201
595 | AdcTubeMeanTemp_FT_D1 | 1434 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | YES | FT 8.201 | YES | FT 4.201
596 | AdcTorBarMeanTemp_FT_D1 | 1438 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | YES | FT 8.201 | YES | FT 4.201
597 | Act_Seuil_H_FT_D1 | 1442 | 0 | BOOL |  | BPCS/PSD | YES | CMD | FT | YES | FT 8.201 | YES | FT 4.201
598 | Seuil_H_FT_D1 | 1444 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | FT | YES | FT 8.201 | YES | FT 4.201
599 | Type_FT_D1 | 1448 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | FT | YES | FT 8.201 | YES | FT 4.201
600 | ScaleMIN_FT_D1 | 3734 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | FT | YES | FT 8.201 | YES | FT 4.201
601 | ScaleMax_FT_D1 | 3738 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | FT | YES | FT 8.201 | YES | FT 4.201
602 | Hyst_FT_D1 | 3766 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | FT | YES | FT 8.201 | YES | FT 4.201
603 | Offset_FT_D1 | 3770 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | FT | YES | FT 8.201 | YES | FT 4.201
604 | Def_Modbus_FTD1 | 4714 | 3 | BOOL | COM Default Modbus FlowMeter (for Both Debimetre) | BPCS/PSD | NO | Defaut | FT | YES | FT 8.201 | YES | FT 4.201
605 | MES_FT_D2 | 1450 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | FT | NO | NA | YES | FT 4.101
606 | MassFlowRate_FT_D2 | 1454 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | NO | NA | YES | FT 4.101
607 | TotalMassFwd_FT_D2 | 1458 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | NO | NA | YES | FT 4.101
608 | TotMassRev_FT_D2 | 1462 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | NO | NA | YES | FT 4.101
609 | AdcTubeMeanTemp_FT_D2 | 1466 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | NO | NA | YES | FT 4.101
610 | AdcTorBarMeanTemp_FT_D2 | 1470 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | NO | NA | YES | FT 4.101
611 | Act_Seuil_H_FT_D2 | 1474 | 0 | BOOL |  | BPCS/PSD | YES | CMD | FT | NO | NA | YES | FT 4.101
612 | Seuil_H_FT_D2 | 1476 | 0 | REAL |  | BPCS/PSD | NO | PRM | FT | NO | NA | YES | FT 4.101
613 | Type_FT_D2 | 1480 | 0 | INT |  | BPCS/PSD | NO | PRM | FT | NO | NA | YES | FT 4.101
614 | ScaleMIN_FT_D2 | 3742 | 0 | REAL |  | BPCS/PSD | NO | PRM | FT | NO | NA | YES | FT 4.101
615 | ScaleMax_FT_D2 | 3746 | 0 | REAL |  | BPCS/PSD | NO | PRM | FT | NO | NA | YES | FT 4.101
616 | Hyst_FT_D2 | 3774 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | FT | NO | NA | YES | FT 4.101
617 | Offset_FT_D2 | 3778 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | FT | NO | NA | YES | FT 4.101
618 | Def_Modbus_FTD2 | 4714 | 4 | BOOL | COM Default Modbus FlowMeter (for Both Debimetre) | BPCS/PSD | NO | Defaut | FT | NO | NA | YES | FT 4.101
619 | MES_FT_D3 | 1482 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | NO | NA | NO | NA
620 | MassFlowRate_FT_D3 | 1486 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | NO | NA | NO | NA
621 | TotalMassFwd_FT_D3 | 1490 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | NO | NA | NO | NA
622 | TotMassRev_FT_D3 | 1494 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | NO | NA | NO | NA
623 | AdcTubeMeanTemp_FT_D3 | 1498 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | NO | NA | NO | NA
624 | AdcTorBarMeanTemp_FT_D3 | 1502 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | NO | NA | NO | NA
625 | Act_Seuil_H_FT_D3 | 1506 | 0 | BOOL |  | BPCS/PSD | YES | CMD | FT | NO | NA | NO | NA
626 | Seuil_H_FT_D3 | 1508 | 0 | REAL |  | BPCS/PSD | NO | PRM | FT | NO | NA | NO | NA
627 | Type_FT_D3 | 1512 | 0 | INT |  | BPCS/PSD | NO | PRM | FT | NO | NA | NO | NA
628 | ScaleMIN_FT_D3 | 3750 | 0 | REAL |  | BPCS/PSD | NO | PRM | FT | NO | NA | NO | NA
629 | ScaleMax_FT_D3 | 3754 | 0 | REAL |  | BPCS/PSD | NO | PRM | FT | NO | NA | NO | NA
630 | Hysteresis_FT_D3 | 3782 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | FT | NO | NA | NO | NA
631 | Offset_FT_D3 | 3786 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | FT | NO | NA | NO | NA
632 | Def_Modbus_FTD3 | 4714 | 5 | BOOL | COM Default Modbus FlowMeter | BPCS/PSD | NO | Defaut | FT | NO | NA | NO | NA
633 | MES_FT_D4 | 1514 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | NO | NA | NO | NA
634 | MassFlowRate_FT_D4 | 1518 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | NO | NA | NO | NA
635 | TotalMassFwd_FT_D4 | 1522 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | NO | NA | NO | NA
636 | TotMassRev_FT_D4 | 1526 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | NO | NA | NO | NA
637 | AdcTubeMeanTemp_FT_D4 | 1530 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | NO | NA | NO | NA
638 | AdcTorBarMeanTemp_FT_D4 | 1534 | 0 | REAL |  | BPCS/PSD | NO | Measure | FT | NO | NA | NO | NA
639 | Act_Seuil_H_FT_D4 | 1538 | 0 | BOOL |  | BPCS/PSD | YES | CMD | FT | NO | NA | NO | NA
640 | Seuil_H_FT_D4 | 1540 | 0 | REAL |  | BPCS/PSD | NO | PRM | FT | NO | NA | NO | NA
641 | Type_FT_D4 | 1544 | 0 | INT |  | BPCS/PSD | NO | PRM | FT | NO | NA | NO | NA
642 | ScaleMIN_FT_D4 | 3758 | 0 | REAL |  | BPCS/PSD | NO | PRM | FT | NO | NA | NO | NA
643 | ScaleMax_FT_D4 | 3762 | 0 | REAL |  | BPCS/PSD | NO | PRM | FT | NO | NA | NO | NA
644 | Hysteresis_FT_D4 | 3790 | 0 | REAL | PRM Hysteresis Sensor | BPCS/PSD | NO | PRM | FT | NO | NA | NO | NA
645 | Offset_FT_D4 | 3794 | 0 | REAL | PRM OFFSET Sensor | BPCS/PSD | NO | PRM | FT | NO | NA | NO | NA
646 | Def_Modbus_FTD4 | 4714 | 6 | BOOL | COM Default Modbus FlowMeter | BPCS/PSD | NO | Defaut | FT | NO | NA | NO | NA
647 | MES_PCV_D1 | 1546 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PCV | YES | PCV 8.201 | YES | PCV 4.201
648 | Val_Simul_PCV_D1 | 1550 | 0 | REAL |  | BPCS/PSD | YES | CMD | PCV | YES | PCV 8.201 | YES | PCV 4.201
649 | Mode_Simul_PCV_D1 | 1554 | 0 | BOOL |  | BPCS/PSD | YES | CMD | PCV | YES | PCV 8.201 | YES | PCV 4.201
650 | PCV_In_Rampe_D1 | 1556 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | YES | PCV 8.201 | YES | PCV 4.201
651 | In_A0_D1 | 1560 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | YES | PCV 8.201 | YES | PCV 4.201
652 | In_A1_D1 | 1564 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | YES | PCV 8.201 | YES | PCV 4.201
653 | In_A2_D1 | 1568 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | YES | PCV 8.201 | YES | PCV 4.201
654 | In_A3_D1 | 1572 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | YES | PCV 8.201 | YES | PCV 4.201
655 | In_P0_D1 | 1576 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | YES | PCV 8.201 | YES | PCV 4.201
656 | In_t0_D1 | 1580 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | YES | PCV 8.201 | YES | PCV 4.201
657 | In_B0_D1 | 1584 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | YES | PCV 8.201 | YES | PCV 4.201
658 | In_B1_D1 | 1588 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | YES | PCV 8.201 | YES | PCV 4.201
659 | RAMPE_VALIDE_D1 | 1592 | 0 | BOOL |  | BPCS/PSD | NO | Status | PCV | NO | PCV 8.201 | NO | PCV 4.201
660 | Figeage_D1 | 1592 | 1 | BOOL |  | BPCS/PSD | NO | Status | PCV | NO | PCV 8.201 | NO | PCV 4.201
661 | ScaleMin_PCV_D1 | 1594 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | PCV | YES | PCV 8.201 | YES | PCV 4.201
662 | ScaleMax_PCV_D1 | 1598 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | PCV | YES | PCV 8.201 | YES | PCV 4.201
663 | Type_PCV_D1 | 1602 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | PCV | YES | PCV 8.201 | YES | PCV 4.201
664 | BP_Figeage_PCV_D1 | 4162 | 4 | BOOL |  | BPCS/PSD | YES | CMD | PCV | YES | PCV 8.201 | YES | PCV 4.201
665 | BP_Valid_RAMPE_PCV_D1 | 4162 | 5 | BOOL |  | BPCS/PSD | YES | CMD | PCV | YES | PCV 8.201 | YES | PCV 4.201
666 | TYPE_RAMPE_PCV_D1 | 4164 | 0 | INT |  | BPCS/PSD | NO | Measure | PCV | YES | PCV 8.201 | YES | PCV 4.201
667 | Cha_Def_PCV_D1 | 4257 | 7 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PCV | YES | PCV 8.201 | YES | PCV 4.201
668 | MES_PCV_D2 | 1604 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | PCV | NO | NA | YES | PCV 4.101
669 | Val_Simul_PCV_D2 | 1608 | 0 | REAL |  | BPCS/PSD | YES | CMD | PCV | NO | NA | YES | PCV 4.101
670 | Mode_Simul_PCV_D2 | 1612 | 0 | BOOL |  | BPCS/PSD | YES | CMD | PCV | NO | NA | YES | PCV 4.101
671 | PCV_In_Rampe_PCV_D2 | 1614 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | YES | PCV 4.101
672 | In_A0_PCV_D2 | 1618 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | YES | PCV 4.101
673 | In_A1_PCV_D2 | 1622 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | YES | PCV 4.101
674 | In_A2_PCV_D2 | 1626 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | YES | PCV 4.101
675 | In_A3_PCV_D2 | 1630 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | YES | PCV 4.101
676 | In_P0_PCV_D2 | 1634 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | YES | PCV 4.101
677 | In_t0_PCV_D2 | 1638 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | YES | PCV 4.101
678 | In_B0_PCV_D2 | 1642 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | YES | PCV 4.101
679 | In_B1_PCV_D2 | 1646 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | YES | PCV 4.101
680 | RAMPE_VALIDE_PCV_D2 | 1650 | 0 | BOOL |  | BPCS/PSD | NO | Status | PCV | NO | NA | NO | PCV 4.101
681 | Figeage_PCV_D2 | 1650 | 1 | BOOL |  | BPCS/PSD | NO | Status | PCV | NO | NA | NO | PCV 4.101
682 | ScaleMin_PCV_D2 | 1652 | 0 | REAL |  | BPCS/PSD | NO | PRM | PCV | NO | NA | YES | PCV 4.101
683 | ScaleMax_PCV_D2 | 1656 | 0 | REAL |  | BPCS/PSD | NO | PRM | PCV | NO | NA | YES | PCV 4.101
684 | Type_PCV_D2 | 1660 | 0 | INT |  | BPCS/PSD | NO | PRM | PCV | NO | NA | YES | PCV 4.101
685 | BP_Figeage_PCV_D2 | 4166 | 0 | BOOL |  | BPCS/PSD | YES | CMD | PCV | NO | NA | YES | PCV 4.101
686 | BP_Valid_RAMPE_PCV_D2 | 4166 | 1 | BOOL |  | BPCS/PSD | YES | CMD | PCV | NO | NA | YES | PCV 4.101
687 | TYPE_RAMPE_PCV_D2 | 4168 | 0 | INT |  | BPCS/PSD | NO | Measure | PCV | NO | NA | YES | PCV 4.101
688 | Cha_Def_PCV_D2 | 4258 | 0 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PCV | NO | NA | YES | PCV 4.101
689 | MES_PCV_D3 | 1662 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
690 | Val_Simul_PCV_D3 | 1666 | 0 | REAL |  | BPCS/PSD | YES | CMD | PCV | NO | NA | NO | NA
691 | Mode_Simul_PCV_D3 | 1670 | 0 | BOOL |  | BPCS/PSD | YES | CMD | PCV | NO | NA | NO | NA
692 | PCV_In_Rampe_PCV_D3 | 1672 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
693 | In_A0_PCV_D3 | 1676 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
694 | In_A1_PCV_D3 | 1680 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
695 | In_A2_PCV_D3 | 1684 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
696 | In_A3_PCV_D3 | 1688 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
697 | In_P0_PCV_D3 | 1692 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
698 | In_t0_PCV_D3 | 1696 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
699 | In_B0_PCV_D3 | 1700 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
700 | In_B1_PCV_D3 | 1704 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
701 | RAMPE_VALIDE_PCV_D3 | 1708 | 0 | BOOL |  | BPCS/PSD | NO | Status | PCV | NO | NA | NO | NA
702 | Figeage_PCV_D3 | 1708 | 1 | BOOL |  | BPCS/PSD | NO | Status | PCV | NO | NA | NO | NA
703 | ScaleMin_PCV_D3 | 1710 | 0 | REAL |  | BPCS/PSD | NO | PRM | PCV | NO | NA | NO | NA
704 | ScaleMax_PCV_D3 | 1714 | 0 | REAL |  | BPCS/PSD | NO | PRM | PCV | NO | NA | NO | NA
705 | Type_PCV_D3 | 1718 | 0 | INT |  | BPCS/PSD | NO | PRM | PCV | NO | NA | NO | NA
706 | BP_Figeage_PCV_D3 | 4170 | 0 | BOOL |  | BPCS/PSD | YES | CMD | PCV | NO | NA | NO | NA
707 | BP_Valid_RAMPE_PCV_D3 | 4170 | 1 | BOOL |  | BPCS/PSD | YES | CMD | PCV | NO | NA | NO | NA
708 | TYPE_RAMPE_PCV_D3 | 4172 | 0 | INT |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
709 | Cha_Def_PCV_D3 | 4258 | 1 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PCV | NO | NA | NO | NA
710 | MES_PCV_D4 | 1720 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
711 | Val_Simul_PCV_D4 | 1724 | 0 | REAL |  | BPCS/PSD | YES | CMD | PCV | NO | NA | NO | NA
712 | Mode_Simul_PCV_D4 | 1728 | 0 | BOOL |  | BPCS/PSD | YES | CMD | PCV | NO | NA | NO | NA
713 | PCV_In_Rampe_PCV_D4 | 1730 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
714 | In_A0_PCV_D4 | 1734 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
715 | In_A1_PCV_D4 | 1738 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
716 | In_A2_PCV_D4 | 1742 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
717 | In_A3_PCV_D4 | 1746 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
718 | In_P0_PCV_D4 | 1750 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
719 | In_t0_PCV_D4 | 1754 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
720 | In_B0_PCV_D4 | 1758 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
721 | In_B1_PCV_D4 | 1762 | 0 | REAL |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
722 | RAMPE_VALIDE_PCV_D4 | 1766 | 0 | BOOL |  | BPCS/PSD | NO | Status | PCV | NO | NA | NO | NA
723 | Figeage_PCV_D4 | 1766 | 1 | BOOL |  | BPCS/PSD | NO | Status | PCV | NO | NA | NO | NA
724 | ScaleMin_PCV_D4 | 1768 | 0 | REAL |  | BPCS/PSD | NO | PRM | PCV | NO | NA | NO | NA
725 | ScaleMax_PCV_D4 | 1772 | 0 | REAL |  | BPCS/PSD | NO | PRM | PCV | NO | NA | NO | NA
726 | Type_PCV_D4 | 1776 | 0 | INT |  | BPCS/PSD | NO | PRM | PCV | NO | NA | NO | NA
727 | BP_Figeage_PCV_D4 | 4174 | 0 | BOOL |  | BPCS/PSD | YES | CMD | PCV | NO | NA | NO | NA
728 | BP_Valid_RAMPE_PCV_D4 | 4174 | 1 | BOOL |  | BPCS/PSD | YES | CMD | PCV | NO | NA | NO | NA
729 | TYPE_RAMPE_PCV_D4 | 4176 | 0 | INT |  | BPCS/PSD | NO | Measure | PCV | NO | NA | NO | NA
730 | Cha_Def_PCV_D4 | 4258 | 2 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | PCV | NO | NA | NO | NA
731 | MES_TT_Exch_1_D1 | 1778 | 0 | REAL | E1_1 | BPCS/PSD | NO | Measure | TT | YES | TT 8.204 | YES | TT 4.204
732 | ScaleMIN_TT_Exch_1_D1 | 1782 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | TT | YES | TT 8.204 | YES | TT 4.204
733 | ScaleMAX_TT_Exch_1_D1 | 1786 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | TT | YES | TT 8.204 | YES | TT 4.204
734 | ModeSimu_TT_Exch_1_D1 | 1790 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | TT | YES | TT 8.204 | YES | TT 4.204
735 | CMDSimu_TT_Exch_1_D1 | 1792 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | TT | YES | TT 8.204 | YES | TT 4.204
736 | ActPSDSL_TT_Exch_1_D1 | 1796 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
737 | PSDSL_TT_Exch_1_D1 | 1798 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
738 | ActPSDSH_TT_Exch_1_D1 | 1802 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
739 | PSDSH_TT_Exch_1_D1 | 1804 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
740 | Type_TT_Exch_1_D1 | 1808 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | TT | YES | TT 8.204 | YES | TT 4.204
741 | Cha_Def_Exch_1_D1 | 4253 | 3 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | YES | TT 8.204 | YES | TT 4.204
742 | MES_TT_Exch_2_D1 | 1810 | 0 | REAL | E1_3 | BPCS/PSD | NO | Measure | TT | YES | TT 8.206 | NO | NA
743 | ScaleMIN_TT_Exch_2_D1 | 1814 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | TT | YES | TT 8.206 | NO | NA
744 | ScaleMAX_TT_Exch_2_D1 | 1818 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | TT | YES | TT 8.206 | NO | NA
745 | ModeSimu_TT_Exch_2_D1 | 1822 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | TT | YES | TT 8.206 | NO | NA
746 | CMDSimu_TT_Exch_2_D1 | 1824 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | TT | YES | TT 8.206 | NO | NA
747 | ActPSDSL_TT_Exch_2_D1 | 1828 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
748 | PSDSL_TT_Exch_2_D1 | 1830 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
749 | ActPSDSH_TT_Exch_2_D1 | 1834 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
750 | PSDSH_TT_Exch_2_D1 | 1836 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
751 | Type_TT_Exch_2_D1 | 1840 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | TT | YES | TT 8.206 | NO | NA
752 | Cha_Def_Exch_2_D1 | 4253 | 4 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | YES | TT 8.206 | NO | NA
753 | MES_TT_Exch_3_D1 | 1842 | 0 | REAL | E1_4 | BPCS/PSD | NO | Measure | TT | YES | TT 8.207 | NO | NA
754 | ScaleMIN_TT_Exch_3_D1 | 1846 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | TT | YES | TT 8.207 | NO | NA
755 | ScaleMAX_TT_Exch_3_D1 | 1850 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | TT | YES | TT 8.207 | NO | NA
756 | ModeSimu_TT_Exch_3_D1 | 1854 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | TT | YES | TT 8.207 | NO | NA
757 | CMDSimu_TT_Exch_3_D1 | 1856 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | TT | YES | TT 8.207 | NO | NA
758 | ActPSDSL_TT_Exch_3_D1 | 1860 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
759 | PSDSL_TT_Exch_3_D1 | 1862 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
760 | ActPSDSH_TT_Exch_3_D1 | 1866 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
761 | PSDSH_TT_Exch_3_D1 | 1868 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
762 | Type_TT_Exch_3_D1 | 1872 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | TT | YES | TT 8.207 | NO | NA
763 | Cha_Def_Exch_3_D1 | 4253 | 5 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | YES | TT 8.207 | NO | NA
764 | MES_TT_Exch_4_D1 | 1874 | 0 | REAL | ALU INF | BPCS/PSD | NO | Measure | TT | YES | TT 8.208 | NO | NA
765 | ScaleMIN_TT_Exch_4_D1 | 1878 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | TT | YES | TT 8.208 | NO | NA
766 | ScaleMAX_TT_Exch_4_D1 | 1882 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | TT | YES | TT 8.208 | NO | NA
767 | ModeSimu_TT_Exch_4_D1 | 1886 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | TT | YES | TT 8.208 | NO | NA
768 | CMDSimu_TT_Exch_4_D1 | 1888 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | TT | YES | TT 8.208 | NO | NA
769 | ActPSDSL_TT_Exch_4_D1 | 1892 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
770 | PSDSL_TT_Exch_4_D1 | 1894 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
771 | ActPSDSH_TT_Exch_4_D1 | 1898 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
772 | PSDSH_TT_Exch_4_D1 | 1900 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
773 | Type_TT_Exch_4_D1 | 1904 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | TT | YES | TT 8.208 | NO | NA
774 | Cha_Def_Exch_4_D1 | 4253 | 6 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | YES | TT 8.208 | NO | NA
775 | MES_TT_Exch_5_D1 | 1906 | 0 | REAL | ALU SUP | BPCS/PSD | NO | Measure | TT | YES | TT 8.205 | NO | NA
776 | ScaleMIN_TT_Exch_5_D1 | 1910 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | TT | YES | TT 8.205 | NO | NA
777 | ScaleMAX_TT_Exch_5_D1 | 1914 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | TT | YES | TT 8.205 | NO | NA
778 | ModeSimu_TT_Exch_5_D1 | 1918 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | TT | YES | TT 8.205 | NO | NA
779 | CMDSimu_TT_Exch_5_D1 | 1920 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | TT | YES | TT 8.205 | NO | NA
780 | ActPSDSL_TT_Exch_5_D1 | 1924 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
781 | PSDSL_TT_Exch_5_D1 | 1926 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
782 | ActPSDSH_TT_Exch_5_D1 | 1930 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
783 | PSDSH_TT_Exch_5_D1 | 1932 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
784 | Type_TT_Exch_5_D1 | 1936 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | TT | YES | TT 8.205 | NO | NA
785 | Cha_Def_Exch_5_D1 | 4253 | 7 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | YES | TT 8.205 | NO | NA
786 | MES_TT_Exch_1_D2 | 1938 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
787 | ScaleMIN_TT_Exch_1_D2 | 1942 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
788 | ScaleMAX_TT_Exch_1_D2 | 1946 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
789 | ModeSimu_TT_Exch_1_D2 | 1950 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
790 | CMDSimu_TT_Exch_1_D2 | 1952 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
791 | ActPSDSL_TT_Exch_1_D2 | 1956 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
792 | PSDSL_TT_Exch_1_D2 | 1958 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
793 | ActPSDSH_TT_Exch_1_D2 | 1962 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
794 | PSDSH_TT_Exch_1_D2 | 1964 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
795 | Type_TT_Exch_1_D2 | 1968 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
796 | Cha_Def_Exch_1_D2 | 4254 | 0 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
797 | MES_TT_Exch_2_D2 | 1970 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
798 | ScaleMIN_TT_Exch_2_D2 | 1974 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
799 | ScaleMAX_TT_Exch_2_D2 | 1978 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
800 | ModeSimu_TT_Exch_2_D2 | 1982 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
801 | CMDSimu_TT_Exch_2_D2 | 1984 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
802 | ActPSDSL_TT_Exch_2_D2 | 1988 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
803 | PSDSL_TT_Exch_2_D2 | 1990 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
804 | ActPSDSH_TT_Exch_2_D2 | 1994 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
805 | PSDSH_TT_Exch_2_D2 | 1996 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
806 | Type_TT_Exch_2_D2 | 2000 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
807 | Cha_Def_Exch_2_D2 | 4254 | 1 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
808 | MES_TT_Exch_3_D2 | 2002 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
809 | ScaleMIN_TT_Exch_3_D2 | 2006 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
810 | ScaleMAX_TT_Exch_3_D2 | 2010 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
811 | ModeSimu_TT_Exch_3_D2 | 2014 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
812 | CMDSimu_TT_Exch_3_D2 | 2016 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
813 | ActPSDSL_TT_Exch_3_D2 | 2020 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
814 | PSDSL_TT_Exch_3_D2 | 2022 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
815 | ActPSDSH_TT_Exch_3_D2 | 2026 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
816 | PSDSH_TT_Exch_3_D2 | 2028 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
817 | Type_TT_Exch_3_D2 | 2032 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
818 | Cha_Def_Exch_3_D2 | 4254 | 2 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
819 | MES_TT_Exch_4_D2 | 2034 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
820 | ScaleMIN_TT_Exch_4_D2 | 2038 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
821 | ScaleMAX_TT_Exch_4_D2 | 2042 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
822 | ModeSimu_TT_Exch_4_D2 | 2046 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
823 | CMDSimu_TT_Exch_4_D2 | 2048 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
824 | ActPSDSL_TT_Exch_4_D2 | 2052 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
825 | PSDSL_TT_Exch_4_D2 | 2054 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
826 | ActPSDSH_TT_Exch_4_D2 | 2058 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
827 | PSDSH_TT_Exch_4_D2 | 2060 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
828 | Type_TT_Exch_4_D2 | 2064 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
829 | Cha_Def_Exch_4_D2 | 4254 | 3 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
830 | MES_TT_Exch_5_D2 | 2066 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
831 | ScaleMIN_TT_Exch_5_D2 | 2070 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
832 | ScaleMAX_TT_Exch_5_D2 | 2074 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
833 | ModeSimu_TT_Exch_5_D2 | 2078 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
834 | CMDSimu_TT_Exch_5_D2 | 2080 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
835 | ActPSDSL_TT_Exch_5_D2 | 2084 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
836 | PSDSL_TT_Exch_5_D2 | 2086 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
837 | ActPSDSH_TT_Exch_5_D2 | 2090 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
838 | PSDSH_TT_Exch_5_D2 | 2092 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
839 | Type_TT_Exch_5_D2 | 2096 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
840 | Cha_Def_Exch_5_D2 | 4254 | 4 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
841 | MES_TT_Exch_1_D3 | 2098 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
842 | ScaleMIN_TT_Exch_1_D3 | 2102 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
843 | ScaleMAX_TT_Exch_1_D3 | 2106 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
844 | ModeSimu_TT_Exch_1_D3 | 2110 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
845 | CMDSimu_TT_Exch_1_D3 | 2112 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
846 | ActPSDSL_TT_Exch_1_D3 | 2116 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
847 | PSDSL_TT_Exch_1_D3 | 2118 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
848 | ActPSDSH_TT_Exch_1_D3 | 2122 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
849 | PSDSH_TT_Exch_1_D3 | 2124 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
850 | Type_TT_Exch_1_D3 | 2128 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
851 | Cha_Def_Exch_1_D3 | 4254 | 5 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
852 | MES_TT_Exch_2_D3 | 2130 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
853 | ScaleMIN_TT_Exch_2_D3 | 2134 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
854 | ScaleMAX_TT_Exch_2_D3 | 2138 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
855 | ModeSimu_TT_Exch_2_D3 | 2142 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
856 | CMDSimu_TT_Exch_2_D3 | 2144 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
857 | ActPSDSL_TT_Exch_2_D3 | 2148 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
858 | PSDSL_TT_Exch_2_D3 | 2150 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
859 | ActPSDSH_TT_Exch_2_D3 | 2154 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
860 | PSDSH_TT_Exch_2_D3 | 2156 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
861 | Type_TT_Exch_2_D3 | 2160 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
862 | Cha_Def_Exch_2_D3 | 4254 | 6 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
863 | MES_TT_Exch_3_D3 | 2162 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
864 | ScaleMIN_TT_Exch_3_D3 | 2166 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
865 | ScaleMAX_TT_Exch_3_D3 | 2170 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
866 | ModeSimu_TT_Exch_3_D3 | 2174 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
867 | CMDSimu_TT_Exch_3_D3 | 2176 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
868 | ActPSDSL_TT_Exch_3_D3 | 2180 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
869 | PSDSL_TT_Exch_3_D3 | 2182 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
870 | ActPSDSH_TT_Exch_3_D3 | 2186 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
871 | PSDSH_TT_Exch_3_D3 | 2188 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
872 | Type_TT_Exch_3_D3 | 2192 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
873 | Cha_Def_Exch_3_D3 | 4254 | 7 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
874 | MES_TT_Exch_4_D3 | 2194 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
875 | ScaleMIN_TT_Exch_4_D3 | 2198 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
876 | ScaleMAX_TT_Exch_4_D3 | 2202 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
877 | ModeSimu_TT_Exch_4_D3 | 2206 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
878 | CMDSimu_TT_Exch_4_D3 | 2208 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
879 | ActPSDSL_TT_Exch_4_D3 | 2212 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
880 | PSDSL_TT_Exch_4_D3 | 2214 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
881 | ActPSDSH_TT_Exch_4_D3 | 2218 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
882 | PSDSH_TT_Exch_4_D3 | 2220 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
883 | Type_TT_Exch_4_D3 | 2224 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
884 | Cha_Def_Exch_4_D3 | 4255 | 0 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
885 | MES_TT_Exch_5_D3 | 2226 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
886 | ScaleMIN_TT_Exch_5_D3 | 2230 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
887 | ScaleMAX_TT_Exch_5_D3 | 2234 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
888 | ModeSimu_TT_Exch_5_D3 | 2238 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
889 | CMDSimu_TT_Exch_5_D3 | 2240 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
890 | ActPSDSL_TT_Exch_5_D3 | 2244 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
891 | PSDSL_TT_Exch_5_D3 | 2246 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
892 | ActPSDSH_TT_Exch_5_D3 | 2250 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
893 | PSDSH_TT_Exch_5_D3 | 2252 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
894 | Type_TT_Exch_5_D3 | 2256 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
895 | Cha_Def_Exch_5_D3 | 4255 | 1 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
896 | MES_TT_Exch_1_D4 | 2258 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
897 | ScaleMIN_TT_Exch_1_D4 | 2262 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
898 | ScaleMAX_TT_Exch_1_D4 | 2266 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
899 | ModeSimu_TT_Exch_1_D4 | 2270 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
900 | CMDSimu_TT_Exch_1_D4 | 2272 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
901 | ActPSDSL_TT_Exch_1_D4 | 2276 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
902 | PSDSL_TT_Exch_1_D4 | 2278 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
903 | ActPSDSH_TT_Exch_1_D4 | 2282 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
904 | PSDSH_TT_Exch_1_D4 | 2284 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
905 | Type_TT_Exch_1_D4 | 2288 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
906 | Cha_Def_Exch_1_D4 | 4255 | 2 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
907 | MES_TT_Exch_2_D4 | 2290 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
908 | ScaleMIN_TT_Exch_2_D4 | 2294 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
909 | ScaleMAX_TT_Exch_2_D4 | 2298 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
910 | ModeSimu_TT_Exch_2_D4 | 2302 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
911 | CMDSimu_TT_Exch_2_D4 | 2304 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
912 | ActPSDSL_TT_Exch_2_D4 | 2308 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
913 | PSDSL_TT_Exch_2_D4 | 2310 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
914 | ActPSDSH_TT_Exch_2_D4 | 2314 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
915 | PSDSH_TT_Exch_2_D4 | 2316 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
916 | Type_TT_Exch_2_D4 | 2320 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
917 | Cha_Def_Exch_2_D4 | 4255 | 3 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
918 | MES_TT_Exch_3_D4 | 2322 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
919 | ScaleMIN_TT_Exch_3_D4 | 2326 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
920 | ScaleMAX_TT_Exch_3_D4 | 2330 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
921 | ModeSimu_TT_Exch_3_D4 | 2334 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
922 | CMDSimu_TT_Exch_3_D4 | 2336 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
923 | ActPSDSL_TT_Exch_3_D4 | 2340 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
924 | PSDSL_TT_Exch_3_D4 | 2342 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
925 | ActPSDSH_TT_Exch_3_D4 | 2346 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
926 | PSDSH_TT_Exch_3_D4 | 2348 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
927 | Type_TT_Exch_3_D4 | 2352 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
928 | Cha_Def_Exch_3_D4 | 4255 | 4 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
929 | MES_TT_Exch_4_D4 | 2354 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
930 | ScaleMIN_TT_Exch_4_D4 | 2358 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
931 | ScaleMAX_TT_Exch_4_D4 | 2362 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
932 | ModeSimu_TT_Exch_4_D4 | 2366 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
933 | CMDSimu_TT_Exch_4_D4 | 2368 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
934 | ActPSDSL_TT_Exch_4_D4 | 2372 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
935 | PSDSL_TT_Exch_4_D4 | 2374 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
936 | ActPSDSH_TT_Exch_4_D4 | 2378 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
937 | PSDSH_TT_Exch_4_D4 | 2380 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
938 | Type_TT_Exch_4_D4 | 2384 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
939 | Cha_Def_Exch_4_D4 | 4255 | 5 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
940 | MES_TT_Exch_5_D4 | 2386 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
941 | ScaleMIN_TT_Exch_5_D4 | 2390 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
942 | ScaleMAX_TT_Exch_5_D4 | 2394 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
943 | ModeSimu_TT_Exch_5_D4 | 2398 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
944 | CMDSimu_TT_Exch_5_D4 | 2400 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
945 | ActPSDSL_TT_Exch_5_D4 | 2404 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
946 | PSDSL_TT_Exch_5_D4 | 2406 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
947 | ActPSDSH_TT_Exch_5_D4 | 2410 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
948 | PSDSH_TT_Exch_5_D4 | 2412 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
949 | Type_TT_Exch_5_D4 | 2416 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
950 | Cha_Def_Exch_5_D4 | 4255 | 6 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
951 | MES_TT_UGF_amont_D1 | 2418 | 0 | REAL | GF1 | BPCS/PSD | NO | Measure | TT | YES | TT 80.1 | YES | TT 40.1
952 | ScaleMIN_TT_UGF_amont_D1 | 2422 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | TT | YES | TT 80.1 | YES | TT 40.1
953 | ScaleMAX_TT_UGF_amont_D1 | 2426 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | TT | YES | TT 80.1 | YES | TT 40.1
954 | ModeSimu_TT_UGF_amont_D1 | 2430 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | TT | YES | TT 80.1 | YES | TT 40.1
955 | CMDSimu_TT_UGF_amont_D1 | 2432 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | TT | YES | TT 80.1 | YES | TT 40.1
956 | ActPSDSL_TT_UGF_amont_D1 | 2436 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | TT 40.1
957 | PSDSL_TT_UGF_amont_D1 | 2438 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | TT 40.1
958 | ActPSDSH_TT_UGF_amont_D1 | 2442 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | TT 40.1
959 | PSDSH_TT_UGF_amont_D1 | 2444 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | TT 40.1
960 | Type_TT_UGF_amont_D1 | 2448 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | TT | YES | TT 80.1 | YES | TT 40.1
961 | Cha_Def_UGF_amont_D1 | 4255 | 7 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | YES | TT 80.1 | YES | TT 40.1
962 | MES_TT_UGF_aval_D1 | 2450 | 0 | REAL | GF3 | BPCS/PSD | NO | Measure | TT | YES | TT 80.3 | NO | NA
963 | ScaleMIN_TT_UGF_aval_D1 | 2454 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | TT | YES | TT 80.3 | NO | NA
964 | ScaleMAX_TT_UGF_aval_D1 | 2458 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | TT | YES | TT 80.3 | NO | NA
965 | ModeSimu_TT_UGF_aval_D1 | 2462 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | TT | YES | TT 80.3 | NO | NA
966 | CMDSimu_TT_UGF_aval_D1 | 2464 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | TT | YES | TT 80.3 | NO | NA
967 | ActPSDSL_TT_UGF_aval_D1 | 2468 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
968 | PSDSL_TT_UGF_aval_D1 | 2470 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
969 | ActPSDSH_TT_UGF_aval_D1 | 2474 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
970 | PSDSH_TT_UGF_aval_D1 | 2476 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
971 | Type_TT_UGF_aval_D1 | 2480 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | TT | YES | TT 80.3 | NO | NA
972 | Cha_Def_UGF_aval_D1 | 4256 | 0 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | YES | TT 80.3 | NO | NA
973 | MES_TT_LGF_amont_D1 | 2482 | 0 | REAL | GF2 | BPCS/PSD | NO | Measure | TT | YES | TT 80.2 | NO | NA
974 | ScaleMIN_TT_LGF_amont_D1 | 2486 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | TT | YES | TT 80.2 | NO | NA
975 | ScaleMAX_TT_LGF_amont_D1 | 2490 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | TT | YES | TT 80.2 | NO | NA
976 | ModeSimu_TT_LGF_amont_D1 | 2494 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | TT | YES | TT 80.2 | NO | NA
977 | CMDSimu_TT_LGF_amont_D1 | 2496 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | TT | YES | TT 80.2 | NO | NA
978 | ActPSDSL_TT_LGF_amont_D1 | 2500 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
979 | PSDSL_TT_LGF_amont_D1 | 2502 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
980 | ActPSDSH_TT_LGF_amont_D1 | 2506 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
981 | PSDSH_TT_LGF_amont_D1 | 2508 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
982 | Type_TT_LGF_amont_D1 | 2512 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | TT | YES | TT 80.2 | NO | NA
983 | Cha_Def_LGF_amont_D1 | 4256 | 1 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | YES | TT 80.2 | NO | NA
984 | MES_TT_LGF_aval_D1 | 2514 | 0 | REAL | GF4 | BPCS/PSD | NO | Measure | TT | YES | TT80.4 | NO | NA
985 | ScaleMIN_TT_LGF_aval_D1 | 2518 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | TT | YES | TT80.4 | NO | NA
986 | ScaleMAX_TT_LGF_aval_D1 | 2522 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | TT | YES | TT80.4 | NO | NA
987 | ModeSimu_TT_LGF_aval_D1 | 2526 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | TT | YES | TT80.4 | NO | NA
988 | CMDSimu_TT_LGF_aval_D1 | 2528 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | TT | YES | TT80.4 | NO | NA
989 | ActPSDSL_TT_LGF_aval_D1 | 2532 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
990 | PSDSL_TT_LGF_aval_D1 | 2534 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
991 | ActPSDSH_TT_LGF_aval_D1 | 2538 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
992 | PSDSH_TT_LGF_aval_D1 | 2540 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
993 | Type_TT_LGF_aval_D1 | 2544 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | TT | YES | TT80.4 | NO | NA
994 | Cha_Def_LGF_aval_D1 | 4256 | 2 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | YES | TT80.4 | NO | NA
995 | MES_TT_UGF_amont_D2 | 2546 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
996 | ScaleMIN_TT_UGF_amont_D2 | 2550 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
997 | ScaleMAX_TT_UGF_amont_D2 | 2554 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
998 | ModeSimu_TT_UGF_amont_D2 | 2558 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
999 | CMDSimu_TT_UGF_amont_D2 | 2560 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1000 | ActPSDSL_TT_UGF_amont_D2 | 2564 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1001 | PSDSL_TT_UGF_amont_D2 | 2566 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1002 | ActPSDSH_TT_UGF_amont_D2 | 2570 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1003 | PSDSH_TT_UGF_amont_D2 | 2572 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1004 | Type_TT_UGF_amont_D2 | 2576 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1005 | Cha_Def_UGF_amont_D2 | 4256 | 3 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
1006 | MES_TT_UGF_aval_D2 | 2578 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
1007 | ScaleMIN_TT_UGF_aval_D2 | 2582 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1008 | ScaleMAX_TT_UGF_aval_D2 | 2586 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1009 | ModeSimu_TT_UGF_aval_D2 | 2590 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1010 | CMDSimu_TT_UGF_aval_D2 | 2592 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1011 | ActPSDSL_TT_UGF_aval_D2 | 2596 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1012 | PSDSL_TT_UGF_aval_D2 | 2598 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1013 | ActPSDSH_TT_UGF_aval_D2 | 2602 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1014 | PSDSH_TT_UGF_aval_D2 | 2604 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1015 | Type_TT_UGF_aval_D2 | 2608 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1016 | Cha_Def_UGF_aval_D2 | 4256 | 4 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
1017 | MES_TT_LGF_amont_D2 | 2610 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
1018 | ScaleMIN_TT_LGF_amont_D2 | 2614 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1019 | ScaleMAX_TT_LGF_amont_D2 | 2618 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1020 | ModeSimu_TT_LGF_amont_D2 | 2622 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1021 | CMDSimu_TT_LGF_amont_D2 | 2624 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1022 | ActPSDSL_TT_LGF_amont_D2 | 2628 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1023 | PSDSL_TT_LGF_amont_D2 | 2630 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1024 | ActPSDSH_TT_LGF_amont_D2 | 2634 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1025 | PSDSH_TT_LGF_amont_D2 | 2636 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1026 | Type_TT_LGF_amont_D2 | 2640 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1027 | Cha_Def_LGF_amont_D2 | 4256 | 5 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
1028 | MES_TT_LGF_aval_D2 | 2642 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
1029 | ScaleMIN_TT_LGF_aval_D2 | 2646 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1030 | ScaleMAX_TT_LGF_aval_D2 | 2650 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1031 | ModeSimu_TT_LGF_aval_D2 | 2654 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1032 | CMDSimu_TT_LGF_aval_D2 | 2656 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1033 | ActPSDSL_TT_LGF_aval_D2 | 2660 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1034 | PSDSL_TT_LGF_aval_D2 | 2662 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1035 | ActPSDSH_TT_LGF_aval_D2 | 2666 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1036 | PSDSH_TT_LGF_aval_D2 | 2668 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1037 | Type_TT_LGF_aval_D2 | 2672 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1038 | Cha_Def_LGF_aval_D2 | 4256 | 6 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
1039 | MES_TT_UGF_amont_D3 | 2674 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
1040 | ScaleMIN_TT_UGF_amont_D3 | 2678 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1041 | ScaleMAX_TT_UGF_amont_D3 | 2682 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1042 | ModeSimu_TT_UGF_amont_D3 | 2686 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1043 | CMDSimu_TT_UGF_amont_D3 | 2688 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1044 | ActPSDSL_TT_UGF_amont_D3 | 2692 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1045 | PSDSL_TT_UGF_amont_D3 | 2694 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1046 | ActPSDSH_TT_UGF_amont_D3 | 2698 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1047 | PSDSH_TT_UGF_amont_D3 | 2700 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1048 | Type_TT_UGF_amont_D3 | 2704 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1049 | Cha_Def_UGF_amont_D3 | 4256 | 7 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
1050 | MES_TT_UGF_aval_D3 | 2706 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
1051 | ScaleMIN_TT_UGF_aval_D3 | 2710 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1052 | ScaleMAX_TT_UGF_aval_D3 | 2714 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1053 | ModeSimu_TT_UGF_aval_D3 | 2718 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1054 | CMDSimu_TT_UGF_aval_D3 | 2720 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1055 | ActPSDSL_TT_UGF_aval_D3 | 2724 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1056 | PSDSL_TT_UGF_aval_D3 | 2726 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1057 | ActPSDSH_TT_UGF_aval_D3 | 2730 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1058 | PSDSH_TT_UGF_aval_D3 | 2732 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1059 | Type_TT_UGF_aval_D3 | 2736 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1060 | Cha_Def_UGF_aval_D3 | 4257 | 0 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
1061 | MES_TT_LGF_amont_D3 | 2738 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
1062 | ScaleMIN_TT_LGF_amont_D3 | 2742 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1063 | ScaleMAX_TT_LGF_amont_D3 | 2746 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1064 | ModeSimu_TT_LGF_amont_D3 | 2750 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1065 | CMDSimu_TT_LGF_amont_D3 | 2752 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1066 | ActPSDSL_TT_LGF_amont_D3 | 2756 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1067 | PSDSL_TT_LGF_amont_D3 | 2758 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1068 | ActPSDSH_TT_LGF_amont_D3 | 2762 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1069 | PSDSH_TT_LGF_amont_D3 | 2764 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1070 | Type_TT_LGF_amont_D3 | 2768 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1071 | Cha_Def_LGF_amont_D3 | 4257 | 1 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
1072 | MES_TT_LGF_aval_D3 | 2770 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
1073 | ScaleMIN_TT_LGF_aval_D3 | 2774 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1074 | ScaleMAX_TT_LGF_aval_D3 | 2778 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1075 | ModeSimu_TT_LGF_aval_D3 | 2782 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1076 | CMDSimu_TT_LGF_aval_D3 | 2784 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1077 | ActPSDSL_TT_LGF_aval_D3 | 2788 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1078 | PSDSL_TT_LGF_aval_D3 | 2790 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1079 | ActPSDSH_TT_LGF_aval_D3 | 2794 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1080 | PSDSH_TT_LGF_aval_D3 | 2796 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1081 | Type_TT_LGF_aval_D3 | 2800 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1082 | Cha_Def_LGF_aval_D3 | 4257 | 2 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
1083 | MES_TT_UGF_amont_D4 | 2802 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
1084 | ScaleMIN_TT_UGF_amont_D4 | 2806 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1085 | ScaleMAX_TT_UGF_amont_D4 | 2810 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1086 | ModeSimu_TT_UGF_amont_D4 | 2814 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1087 | CMDSimu_TT_UGF_amont_D4 | 2816 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1088 | ActPSDSL_TT_UGF_amont_D4 | 2820 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1089 | PSDSL_TT_UGF_amont_D4 | 2822 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1090 | ActPSDSH_TT_UGF_amont_D4 | 2826 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1091 | PSDSH_TT_UGF_amont_D4 | 2828 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1092 | Type_TT_UGF_amont_D4 | 2832 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1093 | Cha_Def_UGF_amont_D4 | 4257 | 3 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
1094 | MES_TT_UGF_aval_D4 | 2834 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
1095 | ScaleMIN_TT_UGF_aval_D4 | 2838 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1096 | ScaleMAX_TT_UGF_aval_D4 | 2842 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1097 | ModeSimu_TT_UGF_aval_D4 | 2846 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1098 | CMDSimu_TT_UGF_aval_D4 | 2848 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1099 | ActPSDSL_TT_UGF_aval_D4 | 2852 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1100 | PSDSL_TT_UGF_aval_D4 | 2854 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1101 | ActPSDSH_TT_UGF_aval_D4 | 2858 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1102 | PSDSH_TT_UGF_aval_D4 | 2860 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1103 | Type_TT_UGF_aval_D4 | 2864 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1104 | Cha_Def_UGF_aval_D4 | 4257 | 4 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
1105 | MES_TT_LGF_amont_D4 | 2866 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
1106 | ScaleMIN_TT_LGF_amont_D4 | 2870 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1107 | ScaleMAX_TT_LGF_amont_D4 | 2874 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1108 | ModeSimu_TT_LGF_amont_D4 | 2878 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1109 | CMDSimu_TT_LGF_amont_D4 | 2880 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1110 | ActPSDSL_TT_LGF_amont_D4 | 2884 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1111 | PSDSL_TT_LGF_amont_D4 | 2886 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1112 | ActPSDSH_TT_LGF_amont_D4 | 2890 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1113 | PSDSH_TT_LGF_amont_D4 | 2892 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1114 | Type_TT_LGF_amont_D4 | 2896 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1115 | Cha_Def_LGF_amont_D4 | 4257 | 5 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
1116 | MES_TT_LGF_aval_D4 | 2898 | 0 | REAL |  | BPCS/PSD | NO | Measure | TT | NO | NA | NO | NA
1117 | ScaleMIN_TT_LGF_aval_D4 | 2902 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1118 | ScaleMAX_TT_LGF_aval_D4 | 2906 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1119 | ModeSimu_TT_LGF_aval_D4 | 2910 | 0 | BOOL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1120 | CMDSimu_TT_LGF_aval_D4 | 2912 | 0 | REAL |  | BPCS/PSD | YES | CMD | TT | NO | NA | NO | NA
1121 | ActPSDSL_TT_LGF_aval_D4 | 2916 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1122 | PSDSL_TT_LGF_aval_D4 | 2918 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1123 | ActPSDSH_TT_LGF_aval_D4 | 2922 | 0 | BOOL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1124 | PSDSH_TT_LGF_aval_D4 | 2924 | 0 | REAL |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1125 | Type_TT_LGF_aval_D4 | 2928 | 0 | INT |  | BPCS/PSD | NO | PRM | TT | NO | NA | NO | NA
1126 | Cha_Def_LGF_aval_D4 | 4257 | 6 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | TT | NO | NA | NO | NA
1127 | Etat_VNitrogen | 2930 | 0 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | YES | SDV 1.1 | YES | VFC 30
1128 | Mode_VNitrogen | 2930 | 1 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | YES | SDV 1.1 | YES | VFC 30
1129 | CMD_VNitrogen | 2930 | 2 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | YES | SDV 1.1 | YES | VFC 30
1130 | IDC_Cycle_VNitrogen | 2932 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | SDV 1.1 | YES | VFC 30
1131 | IDC_Hours_VNitrogen | 2936 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | SDV 1.1 | YES | VFC 30
1132 | PRM_Cycle_VNitrogen | 2938 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | SDV 1.1 | YES | VFC 30
1133 | PRM_Hours_VNitrogen | 2942 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | SDV 1.1 | YES | VFC 30
1134 | Reset_IDC_VNitrogen | 2944 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | SDV 1.1 | YES | VFC 30
1135 | APRM_Cycle_Vnitrogen | 4260 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | SDV 1.1 | YES | VFC 30
1136 | APRM_Hours_Vnitrogen | 4264 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | SDV 1.1 | YES | VFC 30
1137 | Def_IDC_Vnitrogen | 4266 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | SDV 1.1 | YES | VFC 30
1138 | Ala_IDC_Vnitrogen | 4266 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | SDV 1.1 | YES | VFC 30
1139 | Def_Elec_Vnitrogen | 4266 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | SDV 1.1 | NO | VFC 30
1140 | Etat_VAlimPlatineAIR | 2944 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | NO | NA
1141 | Mode_VAlimPlatineAIR | 2944 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1142 | CMD_VAlimPlatineAIR | 2944 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1143 | IDC_Cycle_VPlatine | 2946 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1144 | IDC_Hours_VPlatine | 2950 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1145 | PRM_Cycle_VPlatine | 2952 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1146 | PRM_Hours_VPlatine | 2956 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1147 | Reset_IDC_VPlatine | 2958 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | NA
1148 | APRM_Cycle_Vplatine | 4268 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1149 | APRM_Hours_Vplatine | 4272 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1150 | Def_IDC_Vplatine | 4274 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1151 | Ala_IDC_Vplatine | 4274 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | NA
1152 | Def_Elec_VPlatine | 4274 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1153 | Etat_VStk10ToC | 2958 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | YES | Valve 10.1 | YES | VFC 1.1
1154 | Mode_VStk10ToC | 2958 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | YES | Valve 10.1 | YES | VFC 1.1
1155 | CMD_VStk10ToC | 2958 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | YES | Valve 10.1 | YES | VFC 1.1
1156 | IDC_Cycle_VStk10ToC | 2960 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | YES | Valve 10.1 | YES | VFC 1.1
1157 | IDC_Hours_VStk10ToC | 2964 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | YES | Valve 10.1 | YES | VFC 1.1
1158 | PRM_Cycle_VStk10ToC | 2966 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 10.1 | YES | VFC 1.1
1159 | PRM_Hours_VStk10ToC | 2970 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 10.1 | YES | VFC 1.1
1160 | Reset_IDC_VStk10ToC | 2972 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | YES | Valve 10.1 | YES | VFC 1.1
1161 | APRM_Cycle_VStk10ToC | 4276 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 10.1 | YES | VFC 1.1
1162 | APRM_Hours_VStk10ToC | 4280 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 10.1 | YES | VFC 1.1
1163 | Def_IDC_VStk10ToC | 4282 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | YES | Valve 10.1 | YES | VFC 1.1
1164 | Ala_IDC_VStk10ToC | 4282 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | YES | Valve 10.1 | YES | VFC 1.1
1165 | Def_Elec_VStk10ToC | 4282 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | Valve 10.1 | NO | VFC 1.1
1166 | Etat_VCToStk | 2972 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | YES | VFC 2.3
1167 | Mode_VCToStk | 2972 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFC 2.3
1168 | CMD_VCToStk | 2972 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFC 2.3
1169 | IDC_Cycle_VCToStk | 2974 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFC 2.3
1170 | IDC_Hours_VCToStk | 2978 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFC 2.3
1171 | PRM_Cycle_VCToStk | 2980 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 2.3
1172 | PRM_Hours_VCToStk | 2984 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 2.3
1173 | Reset_IDC_VCToStk | 2986 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | YES | VFC 2.3
1174 | APRM_Cycle_VCToStk | 4284 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 2.3
1175 | APRM_Hours_VCToStk | 4288 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 2.3
1176 | Def_IDC_VCToStk | 4290 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | YES | VFC 2.3
1177 | Ala_IDC_VCToStk | 4290 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | YES | VFC 2.3
1178 | Def_Elec_VCToStk | 4290 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | VFC 2.3
1179 | Etat_VRecircul | 2986 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | YES | VFO 2.4
1180 | Mode_VRecircul | 2986 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFO 2.4
1181 | CMD_VRecircul | 2986 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFO 2.4
1182 | IDC_Cycle_VRecircul | 2988 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFO 2.4
1183 | IDC_Hours_VRecircul | 2992 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFO 2.4
1184 | PRM_Cycle_VRecircul | 2994 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFO 2.4
1185 | PRM_Hours_VRecircul | 2998 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFO 2.4
1186 | Reset_IDC_VRecircul | 3000 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | YES | VFO 2.4
1187 | APRM_Cycle_Vrecircul | 4292 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFO 2.4
1188 | APRM_Hours_Vrecircul | 4296 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFO 2.4
1189 | Def_IDC_Vrecircul | 4298 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | YES | VFO 2.4
1190 | Ala_IDC_Vrecircul | 4298 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | YES | VFO 2.4
1191 | Def_Elec_Vrecircul | 4298 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | VFO 2.4
1192 | Etat_VPurgeComp | 3000 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | YES | VFO 2.5
1193 | Mode_VPurgeComp | 3000 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFO 2.5
1194 | CMD_VPurgeComp | 3000 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFO 2.5
1195 | IDC_Cycle_VPurgeComp | 3002 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFO 2.5
1196 | IDC_Hours_VPurgeComp | 3006 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFO 2.5
1197 | PRM_Cycle_VPurgeComp | 3008 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFO 2.5
1198 | PRM_Hours_VPurgeComp | 3012 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFO 2.5
1199 | Reset_IDC_VPurgeComp | 3014 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | YES | VFO 2.5
1200 | APRM_Cycle_VPurgeComp | 4300 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFO 2.5
1201 | APRM_Hours_VPurgeComp | 4304 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFO 2.5
1202 | Def_IDC_VPurgeComp | 4306 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | YES | VFO 2.5
1203 | Ala_IDC_VPurgeComp | 4306 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | YES | VFO 2.5
1204 | Def_Elec_VPurgeComp | 4306 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | VFO 2.5
1205 | Etat_VCToStk1 | 3014 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | YES | Valve 7.1 | YES | VFC 3.1
1206 | Mode_VCToStk1 | 3014 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | YES | Valve 7.1 | YES | VFC 3.1
1207 | CMD_VCToStk1 | 3014 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | YES | Valve 7.1 | YES | VFC 3.1
1208 | IDC_Cycle_VCToStk1 | 3016 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | YES | Valve 7.1 | YES | VFC 3.1
1209 | IDC_Hours_VCToStk1 | 3020 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | YES | Valve 7.1 | YES | VFC 3.1
1210 | PRM_Cycle_VCToStk1 | 3022 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 7.1 | YES | VFC 3.1
1211 | PRM_Hours_VCToStk1 | 3026 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 7.1 | YES | VFC 3.1
1212 | Reset_IDC_VCToStk1 | 3028 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | YES | Valve 7.1 | YES | VFC 3.1
1213 | APRM_Cycle_VCToStk1 | 4308 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 7.1 | YES | VFC 3.1
1214 | APRM_Hours_VCToStk1 | 4312 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 7.1 | YES | VFC 3.1
1215 | Def_IDC_VCToStk1 | 4314 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | YES | Valve 7.1 | YES | VFC 3.1
1216 | Ala_IDC_VCToStk1 | 4314 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | YES | Valve 7.1 | YES | VFC 3.1
1217 | Def_Elec_VCToStk1 | 4314 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | VFC 3.1
1218 | Etat_VCToStk2 | 3028 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | YES | Valve 7.2 | YES | VFC 3.2
1219 | Mode_VCToStk2 | 3028 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | YES | Valve 7.2 | YES | VFC 3.2
1220 | CMD_VCToStk2 | 3028 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | YES | Valve 7.2 | YES | VFC 3.2
1221 | IDC_Cycle_VCToStk2 | 3030 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | YES | Valve 7.2 | YES | VFC 3.2
1222 | IDC_Hours_VCToStk2 | 3034 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | YES | Valve 7.2 | YES | VFC 3.2
1223 | PRM_Cycle_VCToStk2 | 3036 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 7.2 | YES | VFC 3.2
1224 | PRM_Hours_VCToStk2 | 3040 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 7.2 | YES | VFC 3.2
1225 | Reset_IDC_VCToStk2 | 3042 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | YES | Valve 7.2 | YES | VFC 3.2
1226 | APRM_Cycle_VCToStk2 | 4316 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 7.2 | YES | VFC 3.2
1227 | APRM_Hours_VCToStk2 | 4320 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 7.2 | YES | VFC 3.2
1228 | Def_IDC_VCToStk2 | 4322 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | YES | Valve 7.2 | YES | VFC 3.2
1229 | Ala_IDC_VCToStk2 | 4322 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | YES | Valve 7.2 | YES | VFC 3.2
1230 | Def_Elec_VCToStk2 | 4322 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | VFC 3.2
1231 | Etat_VCToStk3 | 3042 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | YES | Valve 7.3 | YES | VFC 3.3
1232 | Mode_VCToStk3 | 3042 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | YES | Valve 7.3 | YES | VFC 3.3
1233 | CMD_VCToStk3 | 3042 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | YES | Valve 7.3 | YES | VFC 3.3
1234 | IDC_Cycle_VCToStk3 | 3044 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | YES | Valve 7.3 | YES | VFC 3.3
1235 | IDC_Hours_VCToStk3 | 3048 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | YES | Valve 7.3 | YES | VFC 3.3
1236 | PRM_Cycle_VCToStk3 | 3050 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 7.3 | YES | VFC 3.3
1237 | PRM_Hours_VCToStk3 | 3054 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 7.3 | YES | VFC 3.3
1238 | Reset_IDC_VCToStk3 | 3056 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | YES | Valve 7.3 | YES | VFC 3.3
1239 | APRM_Hours_VCToStk3 | 4324 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 7.3 | YES | VFC 3.3
1240 | APRM_Hours_VCToStk3 | 4328 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 7.3 | YES | VFC 3.3
1241 | Def_IDC_VCToStk3 | 4330 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | YES | Valve 7.3 | YES | VFC 3.3
1242 | Ala_IDC_VCToStk3 | 4330 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | YES | Valve 7.3 | YES | VFC 3.3
1243 | Def_Elec_VCToStk3 | 4330 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | VFC 3.3
1244 | Etat_VCToStk4 | 3056 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | YES | VFC 3.4
1245 | Mode_VCToStk4 | 3056 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFC 3.4
1246 | CMD_VCToStk4 | 3056 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFC 3.4
1247 | IDC_Cycle_VCToStk4 | 3058 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFC 3.4
1248 | IDC_Hours_VCToStk4 | 3062 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFC 3.4
1249 | PRM_Cycle_VCToStk4 | 3064 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 3.4
1250 | PRM_Hours_VCToStk4 | 3068 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 3.4
1251 | Reset_IDC_VCToStk4 | 3070 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | YES | VFC 3.4
1252 | APRM_Cycle_VCToStk4 | 4332 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 3.4
1253 | APRM_Hours_VCToStk4 | 4336 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 3.4
1254 | Def_IDC_VCToStk4 | 4338 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | YES | VFC 3.4
1255 | Ala_IDC_VCToStk4 | 4338 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | YES | VFC 3.4
1256 | Def_Elec_VCToStk4 | 4338 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | VFC 3.4
1257 | Etat_VStk1ToD1 | 3070 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | YES | Valve 8.21 | YES | VFC 4.21
1258 | Mode_VStk1ToD1 | 3070 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | YES | Valve 8.21 | YES | VFC 4.21
1259 | CMD_VStk1ToD1 | 3070 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | YES | Valve 8.21 | YES | VFC 4.21
1260 | IDC_Cycle_VStk1ToD1 | 3072 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | YES | Valve 8.21 | YES | VFC 4.21
1261 | IDC_Hours_VStk1ToD1 | 3076 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | YES | Valve 8.21 | YES | VFC 4.21
1262 | PRM_Cycle_VStk1ToD1 | 3078 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.21 | YES | VFC 4.21
1263 | PRM_Hours_VStk1ToD1 | 3082 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.21 | YES | VFC 4.21
1264 | Reset_IDC_VStk1ToD1 | 3084 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | YES | Valve 8.21 | YES | VFC 4.21
1265 | APRM_Cycle_VStk1ToD1 | 4340 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.21 | YES | VFC 4.21
1266 | APRM_Hours_VStk1ToD1 | 4344 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.21 | YES | VFC 4.21
1267 | Def_IDC_VStk1ToD1 | 4346 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | YES | Valve 8.21 | YES | VFC 4.21
1268 | Ala_IDC_VStk1ToD1 | 4346 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | YES | Valve 8.21 | YES | VFC 4.21
1269 | Def_Elec_VStk1ToD1 | 4346 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | VFC 4.21
1270 | Etat_VStk2ToD1 | 3084 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | YES | Valve 8.22 | YES | VFC 4.22
1271 | Mode_VStk2ToD1 | 3084 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | YES | Valve 8.22 | YES | VFC 4.22
1272 | CMD_VStk2ToD1 | 3084 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | YES | Valve 8.22 | YES | VFC 4.22
1273 | IDC_Cycle_VStk2ToD1 | 3086 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | YES | Valve 8.22 | YES | VFC 4.22
1274 | IDC_Hours_VStk2ToD1 | 3090 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | YES | Valve 8.22 | YES | VFC 4.22
1275 | PRM_Cycle_VStk2ToD1 | 3092 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.22 | YES | VFC 4.22
1276 | PRM_Hours_VStk2ToD1 | 3096 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.22 | YES | VFC 4.22
1277 | Reset_IDC_VStk2ToD1 | 3098 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | YES | Valve 8.22 | YES | VFC 4.22
1278 | APRM_Cycle_VStk2ToD1 | 4348 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.22 | YES | VFC 4.22
1279 | APRM_Cycle_VStk2ToD1 | 4352 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.22 | YES | VFC 4.22
1280 | Def_IDC_VStk2ToD1 | 4354 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | YES | Valve 8.22 | YES | VFC 4.22
1281 | Ala_IDC_VStk2ToD1 | 4354 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | YES | Valve 8.22 | YES | VFC 4.22
1282 | Def_Elec_VStk2ToD1 | 4354 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | VFC 4.22
1283 | Etat_VStk3ToD1 | 3098 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | YES | Valve 8.23 | YES | VFC 4.23
1284 | Mode_VStk3ToD1 | 3098 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | YES | Valve 8.23 | YES | VFC 4.23
1285 | CMD_VStk3ToD1 | 3098 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | YES | Valve 8.23 | YES | VFC 4.23
1286 | IDC_Cycle_VStk3ToD1 | 3100 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | YES | Valve 8.23 | YES | VFC 4.23
1287 | IDC_Hours_VStk3ToD1 | 3104 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | YES | Valve 8.23 | YES | VFC 4.23
1288 | PRM_Cycle_VStk3ToD1 | 3106 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.23 | YES | VFC 4.23
1289 | PRM_Hours_VStk3ToD1 | 3110 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.23 | YES | VFC 4.23
1290 | Reset_IDC_VStk3ToD1 | 3112 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | YES | Valve 8.23 | YES | VFC 4.23
1291 | APRM_Cycle_VStk3ToD1 | 4356 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.23 | YES | VFC 4.23
1292 | APRM_Cycle_VStk3ToD1 | 4360 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.23 | YES | VFC 4.23
1293 | Def_IDC_VStk3ToD1 | 4362 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | YES | Valve 8.23 | YES | VFC 4.23
1294 | Ala_IDC_VStk3ToD1 | 4362 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | YES | Valve 8.23 | YES | VFC 4.23
1295 | Def_Elec_VStk3ToD1 | 4362 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | VFC 4.23
1296 | Etat_VStk4ToD1 | 3112 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | YES | VFC 4.24
1297 | Mode_VStk4ToD1 | 3112 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFC 4.24
1298 | CMD_VStk4ToD1 | 3112 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFC 4.24
1299 | IDC_Cycle_VStk4ToD1 | 3114 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFC 4.24
1300 | IDC_Hours_VStk4ToD1 | 3118 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFC 4.24
1301 | PRM_Cycle_VStk4ToD1 | 3120 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.24
1302 | PRM_Hours_VStk4ToD1 | 3124 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.24
1303 | Reset_IDC_VStk4ToD1 | 3126 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | YES | VFC 4.24
1304 | APRM_Cycle_VStk4ToD1 | 4364 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.24
1305 | APRM_Hours_VStk4ToD1 | 4368 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.24
1306 | Def_IDC_VStk4ToD1 | 4370 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | YES | VFC 4.24
1307 | Ala_IDC_VStk4ToD1 | 4370 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | YES | VFC 4.24
1308 | Def_Elec_VStk4ToD1 | 4370 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | VFC 4.24
1309 | Etat_VStk1ToD2 | 3126 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | YES | VFC 4.11
1310 | Mode_VStk1ToD2 | 3126 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFC 4.11
1311 | CMD_VStk1ToD2 | 3126 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFC 4.11
1312 | IDC_Cycle_VStk1ToD2 | 3128 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFC 4.11
1313 | IDC_Hours_VStk1ToD2 | 3132 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFC 4.11
1314 | PRM_Cycle_VStk1ToD2 | 3134 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.11
1315 | PRM_Hours_VStk1ToD2 | 3138 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.11
1316 | Reset_IDC_VStk1ToD2 | 3140 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | YES | VFC 4.11
1317 | APRM_Cycle_VStk1ToD2 | 4372 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.11
1318 | APRM_Cycle_VStk1ToD2 | 4376 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.11
1319 | Def_IDC_VStk1ToD2 | 4378 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | YES | VFC 4.11
1320 | Ala_IDC_VStk1ToD2 | 4378 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | YES | VFC 4.11
1321 | Def_Elec_VStk1ToD2 | 4378 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | VFC 4.11
1322 | Etat_VStk2ToD2 | 3140 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | YES | VFC 4.12
1323 | Mode_VStk2ToD2 | 3140 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFC 4.12
1324 | CMD_VStk2ToD2 | 3140 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFC 4.12
1325 | IDC_Cycle_VStk2ToD2 | 3142 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFC 4.12
1326 | IDC_Hours_VStk2ToD2 | 3146 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFC 4.12
1327 | PRM_Cycle_VStk2ToD2 | 3148 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.12
1328 | PRM_Hours_VStk2ToD2 | 3152 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.12
1329 | Reset_IDC_VStk2ToD2 | 3154 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | YES | VFC 4.12
1330 | APRM_Cycle_VStk2ToD2 | 4380 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.12
1331 | APRM_Hours_VStk2ToD2 | 4384 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.12
1332 | Def_IDC_VStk2ToD2 | 4386 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | YES | VFC 4.12
1333 | Ala_IDC_VStk2ToD2 | 4386 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | YES | VFC 4.12
1334 | Def_Elec_VStk2ToD2 | 4386 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | VFC 4.12
1335 | Etat_VStk3ToD2 | 3154 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | YES | VFC 4.13
1336 | Mode_VStk3ToD2 | 3154 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFC 4.13
1337 | CMD_VStk3ToD2 | 3154 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFC 4.13
1338 | IDC_Cycle_VStk3ToD2 | 3156 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFC 4.13
1339 | IDC_Hours_VStk3ToD2 | 3160 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFC 4.13
1340 | PRM_Cycle_VStk3ToD2 | 3162 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.13
1341 | PRM_Hours_VStk3ToD2 | 3166 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.13
1342 | Reset_IDC_VStk3ToD2 | 3168 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | YES | VFC 4.13
1343 | APRM_Cycle_VStk3ToD2 | 4388 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.13
1344 | APRM_Hours_VStk3ToD2 | 4392 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.13
1345 | Def_IDC_VStk3ToD2 | 4394 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | YES | VFC 4.13
1346 | Ala_IDC_VStk3ToD2 | 4394 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | YES | VFC 4.13
1347 | Def_Elec_VStk3ToD2 | 4394 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | VFC 4.13
1348 | Etat_VStk4ToD2 | 3168 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | YES | VFC 4.14
1349 | Mode_VStk4ToD2 | 3168 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFC 4.14
1350 | CMD_VStk4ToD2 | 3168 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFC 4.14
1351 | IDC_Cycle_VStk4ToD2 | 3170 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFC 4.14
1352 | IDC_Hours_VStk4ToD2 | 3174 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFC 4.14
1353 | PRM_Cycle_VStk4ToD2 | 3176 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.14
1354 | PRM_Hours_VStk4ToD2 | 3180 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.14
1355 | Reset_IDC_VStk4ToD2 | 3182 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | YES | VFC 4.14
1356 | APRM_Cycle_VStk4ToD2 | 4396 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.14
1357 | APRM_Hours_VStk4ToD2 | 4400 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.14
1358 | Def_IDC_VStk4ToD2 | 4402 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | YES | VFC 4.14
1359 | Ala_IDC_VStk4ToD2 | 4402 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | YES | VFC 4.14
1360 | Def_Elec_VStk4ToD2 | 4402 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | VFC 4.14
1361 | Etat_VPurgeStKD1 | 3182 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | YES | VFO 4.25
1362 | Mode_VPurgeStKD1 | 3182 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFO 4.25
1363 | CMD_VPurgeStKD1 | 3182 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFO 4.25
1364 | IDC_Cycle_VPurgeStKD1 | 3184 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFO 4.25
1365 | IDC_Hours_VPurgeStKD1 | 3188 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFO 4.25
1366 | PRM_Cycle_VPurgeStKD1 | 3190 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFO 4.25
1367 | PRM_Hours_VPurgeStKD1 | 3194 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFO 4.25
1368 | Reset_IDC_VPurgeStKD1 | 3196 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | YES | VFO 4.25
1369 | APRM_Cycle_VPurgeStKD1 | 4404 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFO 4.25
1370 | APRM_Hours_VPurgeStKD1 | 4408 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFO 4.25
1371 | Def_IDC_VPurgeStKD1 | 4410 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | YES | VFO 4.25
1372 | Ala_IDC_VPurgeStKD1 | 4410 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | YES | VFO 4.25
1373 | Def_Elec_VPurgeStKD1 | 4410 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | VFO 4.25
1374 | Etat_VPurgeStKD2 | 3196 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | YES | VFO 4.15
1375 | Mode_VPurgeStKD2 | 3196 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFO 4.15
1376 | CMD_VPurgeStKD2 | 3196 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFO 4.15
1377 | IDC_Cycle_VPurgeStKD2 | 3198 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFO 4.15
1378 | IDC_Hours_VPurgeStKD2 | 3202 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFO 4.15
1379 | PRM_Cycle_VPurgeStKD2 | 3204 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFO 4.15
1380 | PRM_Hours_VPurgeStKD2 | 3208 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFO 4.15
1381 | Reset_IDC_VPurgeStKD2 | 3210 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | YES | VFO 4.15
1382 | APRM_Cycle_VPurgeStKD2 | 4412 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFO 4.15
1383 | APRM_Hours_VPurgeStKD2 | 4416 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFO 4.15
1384 | Def_IDC_VPurgeStKD2 | 4418 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | YES | VFO 4.15
1385 | Ala_IDC_VPurgeStKD2 | 4418 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | YES | VFO 4.15
1386 | Def_Elec_VPurgeStKD2 | 4418 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | VFO 4.15
1387 | Etat_VSDV_STK1 | 3210 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | YES | SDV 7.1 | YES | SDV 3.1
1388 | Mode_VSDV_STK1 | 3210 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | YES | SDV 7.1 | YES | SDV 3.1
1389 | CMD_VSDV_STK1 | 3210 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | YES | SDV 7.1 | YES | SDV 3.1
1390 | IDC_Cycle_VSDV_STK1 | 3212 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1391 | IDC_Hours_VSDV_STK1 | 3216 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1392 | PRM_Cycle_VSDV_STK1 | 3218 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1393 | PRM_Hours_VSDV_STK1 | 3222 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1394 | Reset_IDC_VSDV_STK1 | 3224 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | NA
1395 | APRM_Cycle_VSDV_STK1 | 4420 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1396 | APRM_Hours_VSDV_STK1 | 4424 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1397 | Def_IDC_VSDV_STK1 | 4426 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1398 | Ala_IDC_VSDV_STK1 | 4426 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | NA
1399 | Def_Elec_VSDV_STK1 | 4426 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1400 | Etat_VSDV_STK2 | 3224 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | YES | SDV 7.2 | YES | SDV 3.2
1401 | Mode_VSDV_STK2 | 3224 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | YES | SDV 7.2 | YES | SDV 3.2
1402 | CMD_VSDV_STK2 | 3224 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | YES | SDV 7.2 | YES | SDV 3.2
1403 | IDC_Cycle_VSDV_STK2 | 3226 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1404 | IDC_Hours_VSDV_STK2 | 3230 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1405 | PRM_Cycle_VSDV_STK2 | 3232 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1406 | PRM_Hours_VSDV_STK2 | 3236 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1407 | Reset_IDC_VSDV_STK2 | 3238 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | NA
1408 | APRM_Cycle_VSDV_STK2 | 4428 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1409 | APRM_Hours_VSDV_STK2 | 4432 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1410 | Def_IDC_VSDV_STK2 | 4434 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1411 | Ala_IDC_VSDV_STK2 | 4434 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | NA
1412 | Def_Elec_VSDV_STK2 | 4434 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1413 | Etat_VSDV_STK3 | 3238 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | YES | SDV 7.3 | YES | SDV 3.3
1414 | Mode_VSDV_STK3 | 3238 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | YES | SDV 7.3 | YES | SDV 3.3
1415 | CMD_VSDV_STK3 | 3238 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | YES | SDV 7.3 | YES | SDV 3.3
1416 | IDC_Cycle_VSDV_STK3 | 3240 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1417 | IDC_Hours_VSDV_STK3 | 3244 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1418 | PRM_Cycle_VSDV_STK3 | 3246 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1419 | PRM_Hours_VSDV_STK3 | 3250 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1420 | Reset_IDC_VSDV_STK3 | 3252 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | NA
1421 | APRM_Cycle_VSDV_STK3 | 4436 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1422 | APRM_Hours_VSDV_STK3 | 4440 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1423 | Def_IDC_VSDV_STK3 | 4442 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1424 | Ala_IDC_VSDV_STK3 | 4442 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | NA
1425 | Def_Elec_VSDV_STK3 | 4442 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1426 | Etat_VSDV_STK4 | 3252 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | YES | SDV 3.4
1427 | Mode_VSDV_STK4 | 3252 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | SDV 3.4
1428 | CMD_VSDV_STK4 | 3252 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | SDV 3.4
1429 | IDC_Cycle_VSDV_STK4 | 3254 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1430 | IDC_Hours_VSDV_STK4 | 3258 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1431 | PRM_Cycle_VSDV_STK4 | 3260 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1432 | PRM_Hours_VSDV_STK4 | 3264 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1433 | Reset_IDC_VSDV_STK4 | 3266 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | NA
1434 | APRM_Cycle_VSDV_STK4 | 4444 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1435 | APRM_Hours_VSDV_STK4 | 4448 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1436 | Def_IDC_VSDV_STK4 | 4450 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1437 | Ala_IDC_VSDV_STK4 | 4450 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | NA
1438 | Def_Elec_VSDV_STK4 | 4450 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1439 | Etat_VD1_isol | 3266 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | YES | Valve 8.201 | YES | VFC 4.201
1440 | Mode_VD1_isol | 3266 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | YES | Valve 8.201 | YES | VFC 4.201
1441 | CMD_VD1_isol | 3266 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | YES | Valve 8.201 | YES | VFC 4.201
1442 | IDC_Cycle_VD1_isol | 3268 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | YES | Valve 8.201 | YES | VFC 4.201
1443 | IDC_Hours_VD1_isol | 3272 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | YES | Valve 8.201 | YES | VFC 4.201
1444 | PRM_Cycle_VD1_isol | 3274 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.201 | YES | VFC 4.201
1445 | PRM_Hours_VD1_isol | 3278 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.201 | YES | VFC 4.201
1446 | Reset_IDC_VD1_isol | 3280 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | YES | Valve 8.201 | YES | VFC 4.201
1447 | APRM_Cycle_VD1_isol | 4452 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.201 | YES | VFC 4.201
1448 | APRM_Hours_VD1_isol | 4456 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.201 | YES | VFC 4.201
1449 | Def_IDC_VD1_isol | 4458 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | YES | Valve 8.201 | YES | VFC 4.201
1450 | Ala_IDC_VD1_isol | 4458 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | YES | Valve 8.201 | YES | VFC 4.201
1451 | Def_Elec_VD1_isol | 4458 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | Valve 8.201 | NO | VFC 4.201
1452 | Etat_VD1_Amorc | 3280 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | YES | Valve 8.202 | YES | VFC 4.203
1453 | Mode_VD1_Amorc | 3280 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | YES | Valve 8.202 | YES | VFC 4.203
1454 | CMD_VD1_Amorc | 3280 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | YES | Valve 8.202 | YES | VFC 4.203
1455 | IDC_Cycle_VD1_Amorc | 3282 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | YES | Valve 8.202 | YES | VFC 4.203
1456 | IDC_Hours_VD1_Amorc | 3286 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | YES | Valve 8.202 | YES | VFC 4.203
1457 | PRM_Cycle_VD1_Amorc | 3288 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.202 | YES | VFC 4.203
1458 | PRM_Hours_VD1_Amorc | 3292 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.202 | YES | VFC 4.203
1459 | Reset_IDC_VD1_Amorc | 3294 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | YES | Valve 8.202 | YES | VFC 4.203
1460 | APRM_Cycle_VD1_Amorc | 4460 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.202 | YES | VFC 4.203
1461 | APRM_Hours_VD1_Amorc | 4464 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.202 | YES | VFC 4.203
1462 | Def_IDC_VD1_Amorc | 4466 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | YES | Valve 8.202 | YES | VFC 4.203
1463 | Ala_IDC_VD1_Amorc | 4466 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | YES | Valve 8.202 | YES | VFC 4.203
1464 | Def_Elec_VD1_Amorc | 4466 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | Valve 8.202 | NO | VFC 4.203
1465 | Etat_VD1_Purge | 3294 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | YES | Valve 8.203 | YES | VFO 4.202
1466 | Mode_VD1_Purge | 3294 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | YES | Valve 8.203 | YES | VFO 4.202
1467 | CMD_VD1_Purge | 3294 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | YES | Valve 8.203 | YES | VFO 4.202
1468 | IDC_Cycle_VD1_Purge | 3296 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | YES | Valve 8.203 | YES | VFO 4.202
1469 | IDC_Hours_VD1_Purge | 3300 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | YES | Valve 8.203 | YES | VFO 4.202
1470 | PRM_Cycle_VD1_Purge | 3302 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.203 | YES | VFO 4.202
1471 | PRM_Hours_VD1_Purge | 3306 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.203 | YES | VFO 4.202
1472 | Reset_IDC_VD1_Purge | 3308 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | YES | Valve 8.203 | YES | VFO 4.202
1473 | APRM_Cycle_VD1_Purge | 4468 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.203 | YES | VFO 4.202
1474 | APRM_Hours_VD1_Purge | 4472 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 8.203 | YES | VFO 4.202
1475 | Def_IDC_VD1_Purge | 4474 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | YES | Valve 8.203 | YES | VFO 4.202
1476 | Ala_IDC_VD1_Purge | 4474 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | YES | Valve 8.203 | YES | VFO 4.202
1477 | Def_Elec_VD1_Purge | 4474 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | Valve 8.203 | NO | VFO 4.202
1478 | Etat_VD1_SDV | 3308 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | YES | SDV 8.201 | YES | SDV 4.201
1479 | Mode_VD1_SDV | 3308 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | YES | SDV 8.201 | YES | SDV 4.201
1480 | CMD_VD1_SDV | 3308 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | YES | SDV 8.201 | YES | SDV 4.201
1481 | IDC_Cycle_VD1_SDV | 3310 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | SDV 8.201 | NO | SDV 4.201
1482 | IDC_Hours_VD1_SDV | 3314 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | SDV 8.201 | NO | SDV 4.201
1483 | PRM_Cycle_VD1_SDV | 3316 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | SDV 8.201 | NO | SDV 4.201
1484 | PRM_Hours_VD1_SDV | 3320 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | SDV 8.201 | NO | SDV 4.201
1485 | Reset_IDC_VD1_SDV | 3322 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | SDV 8.201 | NO | SDV 4.201
1486 | APRM_Cycle_VD1_SDV | 4476 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | SDV 8.201 | NO | SDV 4.201
1487 | APRM_Hours_VD1_SDV | 4480 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | SDV 8.201 | NO | SDV 4.201
1488 | Def_IDC_VD1_SDV | 4482 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | SDV 8.201 | NO | SDV 4.201
1489 | Ala_IDC_VD1_SDV | 4482 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | SDV 8.201 | NO | SDV 4.201
1490 | Def_Elec_VD1_SDV | 4482 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | SDV 8.201 | NO | SDV 4.201
1491 | Etat_VD2_isol | 3322 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | YES | VFC 4.101
1492 | Mode_VD2_isol | 3322 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFC 4.101
1493 | CMD_VD2_isol | 3322 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFC 4.101
1494 | IDC_Cycle_VD2_isol | 3324 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFC 4.101
1495 | IDC_Hours_VD2_isol | 3328 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFC 4.101
1496 | PRM_Cycle_VD2_isol | 3330 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.101
1497 | PRM_Hours_VD2_isol | 3334 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.101
1498 | Reset_IDC_VD2_isol | 3336 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | YES | VFC 4.101
1499 | APRM_Cycle_VD2_isol |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.101
1500 | APRM_Hours_VD2_isol |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFC 4.101
1501 | Def_IDC_VD2_isol |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | YES | VFC 4.101
1502 | Ala_IDC_VD2_isol |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | YES | VFC 4.101
1503 | Def_Elec_VD2_isol |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | VFC 4.101
1504 | Etat_VD2_Amorc | 3336 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | NO | NA
1505 | Mode_VD2_Amorc | 3336 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1506 | CMD_VD2_Amorc | 3336 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1507 | IDC_Cycle_VD2_Amorc | 3338 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1508 | IDC_Hours_VD2_Amorc | 3342 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1509 | PRM_Cycle_VD2_Amorc | 3344 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1510 | PRM_Hours_VD2_Amorc | 3348 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1511 | Reset_IDC_VD2_Amorc | 3350 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | NA
1512 | APRM_Cycle_VD2_Amorc |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1513 | APRM_Hours_VD2_Amorc |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1514 | Def_IDC_VD2_Amorc |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1515 | Ala_IDC_VD2_Amorc |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | NA
1516 | Def_Elec_VD2_Amorc |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1517 | Etat_VD2_Purge | 3350 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | YES | VFO 4.2102
1518 | Mode_VD2_Purge | 3350 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFO 4.2102
1519 | CMD_VD2_Purge | 3350 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | VFO 4.2102
1520 | IDC_Cycle_VD2_Purge | 3352 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFO 4.2102
1521 | IDC_Hours_VD2_Purge | 3356 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | YES | VFO 4.2102
1522 | PRM_Cycle_VD2_Purge | 3358 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFO 4.2102
1523 | PRM_Hours_VD2_Purge | 3362 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFO 4.2102
1524 | Reset_IDC_VD2_Purge | 3364 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | YES | VFO 4.2102
1525 | APRM_Cycle_VD2_Purge |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFO 4.2102
1526 | APRM_Hours_VD2_Purge |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | YES | VFO 4.2102
1527 | Def_IDC_VD2_Purge |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | YES | VFO 4.2102
1528 | Ala_IDC_VD2_Purge |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | YES | VFO 4.2102
1529 | Def_Elec_VD2_Purge |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | VFO 4.2102
1530 | Etat_VD2_SDV | 3364 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | YES | SDV 4.101
1531 | Mode_VD2_SDV | 3364 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | SDV 4.101
1532 | CMD_VD2_SDV | 3364 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | YES | SDV 4.101
1533 | IDC_Cycle_VD2_SDV | 3366 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | SDV 4.101
1534 | IDC_Hours_VD2_SDV | 3370 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | SDV 4.101
1535 | PRM_Cycle_VD2_SDV | 3372 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | SDV 4.101
1536 | PRM_Hours_VD2_SDV | 3376 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | SDV 4.101
1537 | Reset_IDC_VD2_SDV | 3378 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | SDV 4.101
1538 | APRM_Cycle_VSDV_STK2 |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | SDV 4.101
1539 | APRM_Hours_VSDV_STK2 |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | SDV 4.101
1540 | Def_IDC_VSDV_STK2 |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | SDV 4.101
1541 | Ala_IDC_VSDV_STK2 |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | SDV 4.101
1542 | Def_Elec_VSDV_STK2 |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | SDV 4.101
1543 | Etat_VD3_isol | 3378 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | NO | NA
1544 | Mode_VD3_isol | 3378 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1545 | CMD_VD3_isol | 3378 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1546 | IDC_Cycle_VD3_isol | 3380 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1547 | IDC_Hours_VD3_isol | 3384 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1548 | PRM_Cycle_VD3_isol | 3386 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1549 | PRM_Hours_VD3_isol | 3390 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1550 | Reset_IDC_VD3_isol | 3392 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | NA
1551 | APRM_Cycle_VD3_isol |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1552 | APRM_Hours_VD3_isol |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1553 | Def_IDC_VD3_isol |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1554 | Ala_IDC_VD3_isol |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | NA
1555 | Def_Elec_VD3_isol |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1556 | Etat_VD3_Amorc | 3392 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | NO | NA
1557 | Mode_VD3_Amorc | 3392 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1558 | CMD_VD3_Amorc | 3392 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1559 | IDC_Cycle_VD3_Amorc | 3394 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1560 | IDC_Hours_VD3_Amorc | 3398 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1561 | PRM_Cycle_VD3_Amorc | 3400 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1562 | PRM_Hours_VD3_Amorc | 3404 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1563 | Reset_IDC_VD3_Amorc | 3406 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | NA
1564 | APRM_Cycle_VD3_Amorc |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1565 | APRM_Hours_VD3_Amorc |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1566 | Def_IDC_VD3_Amorc |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1567 | Ala_IDC_VD3_Amorc |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | NA
1568 | Def_Elec_VD3_Amorc |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1569 | Etat_VD3_Purge | 3406 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | NO | NA
1570 | Mode_VD3_Purge | 3406 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1571 | CMD_VD3_Purge | 3406 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1572 | IDC_Cycle_VD3_Purge | 3408 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1573 | IDC_Hours_VD3_Purge | 3412 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1574 | PRM_Cycle_VD3_Purge | 3414 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1575 | PRM_Hours_VD3_Purge | 3418 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1576 | Reset_IDC_VD3_Purge | 3420 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | NA
1577 | APRM_Cycle_VD3_Purge |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1578 | APRM_Hours_VD3_Purge |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1579 | Def_IDC_VD3_Purge |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1580 | Ala_IDC_VD3_Purge |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | NA
1581 | Def_Elec_VD3_Purge |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1582 | Etat_VD3_SDV | 3420 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | NO | NA
1583 | Mode_VD3_SDV | 3420 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1584 | CMD_VD3_SDV | 3420 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1585 | IDC_Cycle_VD3_SDV | 3422 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1586 | IDC_Hours_VD3_SDV | 3426 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1587 | PRM_Cycle_VD3_SDV | 3428 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1588 | PRM_Hours_VD3_SDV | 3432 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1589 | Reset_IDC_VD3_SDV | 3434 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | NA
1590 | APRM_Cycle_VD3_SDV |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1591 | APRM_Hours_VD3_SDV |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1592 | Def_IDC_VD3_SDV |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1593 | Ala_IDC_VD3_SDV |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | NA
1594 | Def_Elec_VD3_SDV |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1595 | Etat_VD4_isol | 3434 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | NO | NA
1596 | Mode_VD4_isol | 3434 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1597 | CMD_VD4_isol | 3434 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1598 | IDC_Cycle_VD4_isol | 3436 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1599 | IDC_Hours_VD4_isol | 3440 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1600 | PRM_Cycle_VD4_isol | 3442 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1601 | PRM_Hours_VD4_isol | 3446 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1602 | Reset_IDC_VD4_isol | 3448 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | NA
1603 | APRM_Cycle_VD4_isol |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1604 | APRM_Hours_VD4_isol |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1605 | Def_IDC_VD4_isol |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1606 | Ala_IDC_VD4_isol |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | NA
1607 | Def_Elec_VD4_isol |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1608 | Etat_VD4_Amorc | 3448 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | NO | NA
1609 | Mode_VD4_Amorc | 3448 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1610 | CMD_VD4_Amorc | 3448 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1611 | IDC_Cycle_VD4_Amorc | 3450 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1612 | IDC_Hours_VD4_Amorc | 3454 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1613 | PRM_Cycle_VD4_Amorc | 3456 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1614 | PRM_Hours_VD4_Amorc | 3460 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1615 | Reset_IDC_VD4_Amorc | 3462 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | NA
1616 | APRM_Cycle_VD4_Amorc |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1617 | APRM_Hours_VD4_Amorc |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1618 | Def_IDC_VD4_Amorc |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1619 | Ala_IDC_VD4_Amorc |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | NA
1620 | Def_Elec_VD4_Amorc |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1621 | Etat_VD4_Purge | 3462 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | NO | NA
1622 | Mode_VD4_Purge | 3462 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1623 | CMD_VD4_Purge | 3462 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1624 | IDC_Cycle_VD4_Purge | 3464 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1625 | IDC_Hours_VD4_Purge | 3468 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1626 | PRM_Cycle_VD4_Purge | 3470 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1627 | PRM_Hours_VD4_Purge | 3474 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1628 | Reset_IDC_VD4_Purge | 3476 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | NA
1629 | APRM_Cycle_VD4_Purge |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1630 | APRM_Hours_VD4_Purge |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1631 | Def_IDC_VD4_Purge |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1632 | Ala_IDC_VD4_Purge |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | NA
1633 | Def_Elec_VD4_Purge |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1634 | Etat_VD4_SDV | 3476 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | NO | NA
1635 | Mode_VD4_SDV | 3476 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1636 | CMD_VD4_SDV | 3476 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1637 | IDC_Cycle_VD4_SDV | 3478 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1638 | IDC_Hours_VD4_SDV | 3482 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1639 | PRM_Cycle_VD4_SDV | 3484 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1640 | PRM_Hours_VD4_SDV | 3488 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1641 | Reset_IDC_VD4_SDV | 3490 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | NA
1642 | APRM_Cycle_VD4_SDV |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1643 | APRM_Hours_VD4_SDV |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1644 | Def_IDC_VD4_SDV |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1645 | Ala_IDC_VD4_SDV |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | NA
1646 | Def_Elec_VD4_SDV |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1647 | Etat_VPurgeAirComp | 3490 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | YES | Valve 12.1 | YES | ECV 12.1
1648 | Mode_VPurgeAirComp | 3490 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | YES | Valve 12.1 | YES | ECV 12.1
1649 | CMD_VPurgeAirComp | 3490 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | YES | Valve 12.1 | YES | ECV 12.1
1650 | IDC_Cycle_VPurgeAirComp | 3492 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | YES | Valve 12.1 | YES | ECV 12.1
1651 | IDC_Hours_VPurgeAirComp | 3496 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | YES | Valve 12.1 | YES | ECV 12.1
1652 | PRM_Cycle_VPurgeAirComp | 3498 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 12.1 | YES | ECV 12.1
1653 | PRM_Hours_VPurgeAirComp | 3502 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 12.1 | YES | ECV 12.1
1654 | Reset_IDC_VPurgeAirComp | 3504 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | YES | Valve 12.1 | YES | ECV 12.1
1655 | APRM_Cycle_VPurgeAirComp | 4580 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | Valve 12.1 | YES | ECV 12.1
1656 | APRM_Hours_VPurgeAirComp | 4584 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | Valve 12.1 | YES | ECV 12.1
1657 | Def_IDC_VPurgeAirComp | 4586 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | YES | Valve 12.1 | YES | ECV 12.1
1658 | Ala_IDC_VPurgeAirComp | 4586 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | YES | Valve 12.1 | YES | ECV 12.1
1659 | Def_Elec_VPurgeAirComp | 4586 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | Valve 12.1 | NO | ECV 12.1
1660 | Etat_VD1_L_GF | 3504 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | YES | ECV 80.2 | NO | NA
1661 | Mode_VD1_L_GF | 3504 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | YES | ECV 80.2 | NO | NA
1662 | CMD_VD1_L_GF | 3504 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | YES | ECV 80.2 | NO | NA
1663 | IDC_Cycle_VD1_L_GF | 3506 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | YES | ECV 80.2 | NO | NA
1664 | IDC_Hours_VD1_L_GF | 3510 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | YES | ECV 80.2 | NO | NA
1665 | PRM_Cycle_VD1_L_GF | 3512 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | ECV 80.2 | NO | NA
1666 | PRM_Hours_VD1_L_GF | 3516 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | ECV 80.2 | NO | NA
1667 | Reset_IDC_VD1_L_GF | 3518 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | YES | ECV 80.2 | NO | NA
1668 | APRM_Cycle_VD1_L_G | 4588 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | ECV 80.2 | NO | NA
1669 | APRM_Hours_VD1_L_G | 4592 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | ECV 80.2 | NO | NA
1670 | Def_IDC_VD1_L_G | 4594 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | YES | ECV 80.2 | NO | NA
1671 | Ala_IDC_VD1_L_G | 4594 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | YES | ECV 80.2 | NO | NA
1672 | Def_Elec_VD1_L_G | 4594 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1673 | Etat_VD1_U_GF | 3518 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | YES | ECV 80.1 | YES | PCV 40.1
1674 | Mode_VD1_U_GF | 3518 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | YES | ECV 80.1 | YES | PCV 40.1
1675 | CMD_VD1_U_GF | 3518 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | YES | ECV 80.1 | YES | PCV 40.1
1676 | IDC_Cycle_VD1_U_GF | 3520 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | YES | ECV 80.1 | YES | PCV 40.1
1677 | IDC_Hours_VD1_U_GF | 3524 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | YES | ECV 80.1 | YES | PCV 40.1
1678 | PRM_Cycle_VD1_U_GF | 3526 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | ECV 80.1 | YES | PCV 40.1
1679 | PRM_Hours_VD1_U_GF | 3530 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | ECV 80.1 | YES | PCV 40.1
1680 | Reset_IDC_VD1_U_GF | 3532 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | YES | ECV 80.1 | YES | PCV 40.1
1681 | APRM_Cycle_VD1_U_GF | 4596 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | YES | ECV 80.1 | YES | PCV 40.1
1682 | APRM_Hours_VD1_U_GF | 4600 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | YES | ECV 80.1 | YES | PCV 40.1
1683 | Def_IDC_VD1_U_GF | 4602 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | YES | ECV 80.1 | YES | PCV 40.1
1684 | Ala_IDC_VD1_U_GF | 4602 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | YES | ECV 80.1 | YES | PCV 40.1
1685 | Def_Elec_VD1_U_GF | 4602 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1686 | Etat_VD2_L_GF | 3532 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | NO | NA
1687 | Mode_VD2_L_GF | 3532 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1688 | CMD_VD2_L_GF | 3532 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1689 | IDC_Cycle_VD2_L_GF | 3534 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1690 | IDC_Hours_VD2_L_GF | 3538 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1691 | PRM_Cycle_VD2_L_GF | 3540 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1692 | PRM_Hours_VD2_L_GF | 3544 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1693 | Reset_IDC_VD2_L_GF | 3546 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | NA
1694 | APRM_Cycle_VD2_L_GF |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1695 | APRM_Hours_VD2_L_GF |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1696 | Def_IDC_VD2_L_GF |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1697 | Ala_IDC_VD2_L_GF |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | NA
1698 | Def_Elec_VD2_L_GF |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1699 | Etat_VD2_U_GF | 3546 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | NO | NA
1700 | Mode_VD2_U_GF | 3546 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1701 | CMD_VD2_U_GF | 3546 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1702 | IDC_Cycle_VD2_U_GF | 3548 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1703 | IDC_Hours_VD2_U_GF | 3552 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1704 | PRM_Cycle_VD2_U_GF | 3554 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1705 | PRM_Hours_VD2_U_GF | 3558 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1706 | Reset_IDC_VD2_U_GF | 3560 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | NA
1707 | APRM_Cycle_VD2_U_GF |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1708 | APRM_Hours_VD2_U_GF |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1709 | Def_IDC_VD2_U_GF |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1710 | Ala_IDC_VD2_U_GF |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | NA
1711 | Def_Elec_VD2_U_GF |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1712 | Etat_VD3_L_GF | 3560 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | NO | NA
1713 | Mode_VD3_L_GF | 3560 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1714 | CMD_VD3_L_GF | 3560 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1715 | IDC_Cycle_VD3_L_GF | 3562 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1716 | IDC_Hours_VD3_L_GF | 3566 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1717 | PRM_Cycle_VD3_L_GF | 3568 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1718 | PRM_Hours_VD3_L_GF | 3572 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1719 | Reset_IDC_VD3_L_GF | 3574 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | NA
1720 | APRM_Cycle_VD3_L_GF |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1721 | APRM_Hours_VD3_L_GF |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1722 | Def_IDC_VD3_L_GF |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1723 | Ala_IDC_VD3_L_GF |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | NA
1724 | Def_Elec_VD3_L_GF |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1725 | Etat_VD3_U_GF | 3574 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | NO | NA
1726 | Mode_VD3_U_GF | 3574 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1727 | CMD_VD3_U_GF | 3574 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1728 | IDC_Cycle_VD3_U_GF | 3576 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1729 | IDC_Hours_VD3_U_GF | 3580 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1730 | PRM_Cycle_VD3_U_GF | 3582 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1731 | PRM_Hours_VD3_U_GF | 3586 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1732 | Reset_IDC_VD3_U_GF | 3588 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | NA
1733 | APRM_Cycle_VD3_U_GF |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1734 | APRM_Hours_VD3_U_GF |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1735 | Def_IDC_VD3_U_GF |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1736 | Ala_IDC_VD3_U_GF |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | NA
1737 | Def_Elec_VD3_U_GF |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1738 | Etat_VD4_L_GF | 3588 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | NO | NA
1739 | Mode_VD4_L_GF | 3588 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1740 | CMD_VD4_L_GF | 3588 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1741 | IDC_Cycle_VD4_L_GF | 3590 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1742 | IDC_Hours_VD4_L_GF | 3594 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1743 | PRM_Cycle_VD4_L_GF | 3596 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1744 | PRM_Hours_VD4_L_GF | 3600 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1745 | Reset_IDC_VD4_L_GF | 3602 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | NA
1746 | APRM_Cycle_VD4_L_GF |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1747 | APRM_Hours_VD4_L_GF |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1748 | Def_IDC_VD4_L_GF |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1749 | Ala_IDC_VD4_L_GF |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | NA
1750 | Def_Elec_VD4_L_GF |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1751 | Etat_VD4_U_GF | 3602 | 1 | BOOL | Valve Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | Valve | NO | NA | NO | NA
1752 | Mode_VD4_U_GF | 3602 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1753 | CMD_VD4_U_GF | 3602 | 3 | BOOL | Valve CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | Valve | NO | NA | NO | NA
1754 | IDC_Cycle_VD4_U_GF | 3604 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1755 | IDC_Hours_VD4_U_GF | 3608 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | Valve | NO | NA | NO | NA
1756 | PRM_Cycle_VD4_U_GF | 3610 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1757 | PRM_Hours_VD4_U_GF | 3614 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1758 | Reset_IDC_VD4_U_GF | 3616 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | Valve | NO | NA | NO | NA
1759 | APRM_Cycle_VD4_U_GF |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1760 | APRM_Hours_VD4_U_GF |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | Valve | NO | NA | NO | NA
1761 | Def_IDC_VD4_U_GF |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1762 | Ala_IDC_VD4_U_GF |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | Valve | NO | NA | NO | NA
1763 | Def_Elec_VD4_U_GF |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | Valve | NO | NA | NO | NA
1764 | ETAT_CompH2 | 3616 | 1 | BOOL | Motor Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | MOTOR | NO | C2 | YES | C2
1765 | Mode_CompH2 | 3616 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | MOTOR | NO | C2 | YES | C2
1766 | CMD_CompH2 | 3616 | 3 | BOOL | Motor CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | MOTOR | NO | C2 | YES | C2
1767 | IDC_Cycle_CompH2 | 3618 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | MOTOR | NO | C2 | YES | C2
1768 | IDC_Hours_CompH2 | 3622 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | MOTOR | NO | C2 | YES | C2
1769 | PRM_Cycle_CompH2 | 3624 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | MOTOR | NO | C2 | YES | C2
1770 | PRM_Hours_CompH2 | 3628 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | MOTOR | NO | C2 | YES | C2
1771 | Reset_IDC_CompH2 | 3630 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | MOTOR | NO | C2 | YES | C2
1772 | APRM_Cycle_CompH2 | 4652 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | MOTOR | NO | C2 | YES | C2
1773 | APRM_Hours_CompH2 | 4656 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | MOTOR | NO | C2 | YES | C2
1774 | Def_IDC_CompH2 | 4658 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | MOTOR | NO | C2 | YES | C2
1775 | Ala_IDC_CompH2 | 4658 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | MOTOR | NO | C2 | YES | C2
1776 | Def_Elec_CompH2 | 4658 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | MOTOR | NO | C2 | YES | C2
1777 | ETAT_REFCompH2 | 3630 | 1 | BOOL | Motor Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | MOTOR | NO | R80 | YES | R20
1778 | Mode_REFCompH2 | 3630 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | MOTOR | NO | R80 | YES | R20
1779 | CMD_REFCompH2 | 3630 | 3 | BOOL | Motor CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | MOTOR | NO | R80 | YES | R20
1780 | IDC_Cycle_REFCompH2 | 3632 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | MOTOR | NO | R80 | YES | R20
1781 | IDC_Hours_REFCompH2 | 3636 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | MOTOR | NO | R80 | YES | R20
1782 | PRM_Cycle_REFCompH2 | 3638 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | MOTOR | NO | R80 | YES | R20
1783 | PRM_Hours_REFCompH2 | 3642 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | MOTOR | NO | R80 | YES | R20
1784 | Reset_IDC_REFCompH2 | 3644 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | MOTOR | NO | R80 | YES | R20
1785 | APRM_Cycle_REFCompH2 | 4660 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | MOTOR | NO | R80 | YES | R20
1786 | APRM_Hours_REFCompH2 | 4664 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | MOTOR | NO | R80 | YES | R20
1787 | Def_IDC_REFCompH2 | 4666 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | MOTOR | NO | R80 | YES | R20
1788 | Ala_IDC_REFCompH2 | 4666 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | MOTOR | NO | R80 | YES | R20
1789 | Def_Elec_REFCompH2 | 4666 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | MOTOR | NO | R80 | YES | R20
1790 | ETAT_AirComp | 3644 | 1 | BOOL | Motor Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | MOTOR | YES | C12.1 | YES | C 12.1 / C 12.2
1791 | Mode_AirComp | 3644 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | MOTOR | YES | C12.1 | YES | C 12.1 / C 12.2
1792 | CMD_AirComp | 3644 | 3 | BOOL | Motor CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | MOTOR | YES | C12.1 | YES | C 12.1 / C 12.2
1793 | IDC_Cycle_AirComp | 3646 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | MOTOR | YES | C12.1 | YES | C 12.1 / C 12.2
1794 | IDC_Hours_AirComp | 3650 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | MOTOR | YES | C12.1 | YES | C 12.1 / C 12.2
1795 | PRM_Cycle_AirComp | 3652 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | MOTOR | YES | C12.1 | YES | C 12.1 / C 12.2
1796 | PRM_Hours_AirComp | 3656 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | MOTOR | YES | C12.1 | YES | C 12.1 / C 12.2
1797 | Reset_IDC_AirComp | 3658 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | MOTOR | YES | C12.1 | YES | C 12.1 / C 12.2
1798 | APRM_Cycle_AirComp | 4668 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | MOTOR | YES | C12.1 | YES | C 12.1 / C 12.2
1799 | APRM_Hours_AirComp | 4672 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | MOTOR | YES | C12.1 | YES | C 12.1 / C 12.2
1800 | Def_IDC_AirComp | 4674 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | MOTOR | YES | C12.1 | YES | C 12.1 / C 12.2
1801 | Ala_IDC_AirComp | 4674 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | MOTOR | YES | C12.1 | YES | C 12.1 / C 12.2
1802 | Def_Elec_AirComp | 4674 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | MOTOR | YES | C12.1 | YES | C 12.1 / C 12.2
1803 | ETAT_AirExctractor | 3658 | 1 | BOOL | Motor Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | MOTOR | YES | C22 A/B/C | YES | C 21
1804 | Mode_AirExctractor | 3658 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | MOTOR | YES | C22 A/B/C | YES | C 21
1805 | CMD_AirExctractor | 3658 | 3 | BOOL | Motor CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | MOTOR | YES | C22 A/B/C | YES | C 21
1806 | IDC_Cycle_AirExctractor | 3660 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | MOTOR | YES | C22 A/B/C | YES | C 21
1807 | IDC_Hours_AirExctractor | 3664 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | MOTOR | YES | C22 A/B/C | YES | C 21
1808 | PRM_Cycle_AirExctractor | 3666 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | MOTOR | YES | C22 A/B/C | YES | C 21
1809 | PRM_Hours_AirExctractor | 3670 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | MOTOR | YES | C22 A/B/C | YES | C 21
1810 | Reset_IDC_AirExctractor | 3672 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | MOTOR | YES | C22 A/B/C | YES | C 21
1811 | APRM_Cycle_AirExctractor | 4676 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | MOTOR | YES | C22 A/B/C | YES | C 21
1812 | APRM_Hours_AirExctractor | 4680 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | MOTOR | YES | C22 A/B/C | YES | C 21
1813 | Def_IDC_AirExctractor | 4682 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | MOTOR | YES | C22 A/B/C | YES | C 21
1814 | Ala_IDC_AirExctractor | 4682 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | MOTOR | YES | C22 A/B/C | YES | C 21
1815 | Def_Elec_AirExctractor | 4682 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | MOTOR | YES | C22 A/B/C | YES | C 21
1816 | ETAT_D1_Exch | 3672 | 1 | BOOL | Motor Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | MOTOR | YES | E 8.201 | YES | R 40
1817 | Mode_D1_Exch | 3672 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | MOTOR | YES | E 8.201 | YES | R 40
1818 | CMD_D1_Exch | 3672 | 3 | BOOL | Motor CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | MOTOR | YES | E 8.201 | YES | R 40
1819 | IDC_Cycle_D1_Exch | 3674 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | MOTOR | YES | E 8.201 | YES | R 40
1820 | IDC_Hours_D1_Exch | 3678 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | MOTOR | YES | E 8.201 | YES | R 40
1821 | PRM_Cycle_D1_Exch | 3680 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | MOTOR | YES | E 8.201 | YES | R 40
1822 | PRM_Hours_D1_Exch | 3684 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | MOTOR | YES | E 8.201 | YES | R 40
1823 | Reset_IDC_D1_Exch | 3686 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | MOTOR | YES | E 8.201 | YES | R 40
1824 | APRM_Cycle_D1_Exch | 4684 | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | MOTOR | YES | E 8.201 | YES | R 40
1825 | APRM_Hours_D1_Exch | 4688 | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | MOTOR | YES | E 8.201 | YES | R 40
1826 | Def_IDC_D1_Exch | 4690 | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | MOTOR | YES | E 8.201 | YES | R 40
1827 | Ala_IDC_D1_Exch | 4690 | 1 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | MOTOR | YES | E 8.201 | YES | R 40
1828 | Def_Elec_D1_Exch | 4690 | 2 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | MOTOR | YES | E 8.201 | YES | R 40
1829 | ETAT_D2_Exch | 3686 | 1 | BOOL | Motor Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | MOTOR | NO | NA | NO | NA
1830 | Mode_D2_Exch | 3686 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | MOTOR | NO | NA | NO | NA
1831 | CMD_D2_Exch | 3686 | 3 | BOOL | Motor CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | MOTOR | NO | NA | NO | NA
1832 | IDC_Cycle_D2_Exch | 3688 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | MOTOR | NO | NA | NO | NA
1833 | IDC_Hours_D2_Exch | 3692 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | MOTOR | NO | NA | NO | NA
1834 | PRM_Cycle_D2_Exch | 3694 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | MOTOR | NO | NA | NO | NA
1835 | PRM_Hours_D2_Exch | 3698 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | MOTOR | NO | NA | NO | NA
1836 | Reset_IDC_D2_Exch | 3700 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | MOTOR | NO | NA | NO | NA
1837 | APRM_Cycle_D2_Exch |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | MOTOR | NO | NA | NO | NA
1838 | APRM_Hours_D2_Exch |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | MOTOR | NO | NA | NO | NA
1839 | Def_IDC_D2_Exch |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | MOTOR | NO | NA | NO | NA
1840 | Ala_IDC_D2_Exch |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | MOTOR | NO | NA | NO | NA
1841 | Def_Elec_D2_Exch |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | MOTOR | NO | NA | NO | NA
1842 | ETAT_D3_Exch | 3700 | 1 | BOOL | Motor Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | MOTOR | NO | NA | NO | NA
1843 | Mode_D3_Exch | 3700 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | MOTOR | NO | NA | NO | NA
1844 | CMD_D3_Exch | 3700 | 3 | BOOL | Motor CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | MOTOR | NO | NA | NO | NA
1845 | IDC_Cycle_D3_Exch | 3702 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | MOTOR | NO | NA | NO | NA
1846 | IDC_Hours_D3_Exch | 3706 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | MOTOR | NO | NA | NO | NA
1847 | PRM_Cycle_D3_Exch | 3708 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | MOTOR | NO | NA | NO | NA
1848 | PRM_Hours_D3_Exch | 3712 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | MOTOR | NO | NA | NO | NA
1849 | Reset_IDC_D3_Exch | 3714 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | MOTOR | NO | NA | NO | NA
1850 | APRM_Cycle_D3_Exch |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | MOTOR | NO | NA | NO | NA
1851 | APRM_Hours_D3_Exch |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | MOTOR | NO | NA | NO | NA
1852 | Def_IDC_D3_Exch |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | MOTOR | NO | NA | NO | NA
1853 | Ala_IDC_D3_Exch |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | MOTOR | NO | NA | NO | NA
1854 | Def_Elec_D3_Exch |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | MOTOR | NO | NA | NO | NA
1855 | ETAT_D4_Exch | 3714 | 1 | BOOL | Motor Status, 1 = Open, 0= Closed | BPCS/PSD | NO | Status | MOTOR | NO | NA | NO | NA
1856 | Mode_D4_Exch | 3714 | 2 | BOOL | Mode Forcage, 1 = Activate, 0= Deactivate | BPCS/PSD | YES | CMD | MOTOR | NO | NA | NO | NA
1857 | CMD_D4_Exch | 3714 | 3 | BOOL | Motor CMD, 1 = Open, 0= Closed | BPCS/PSD | YES | CMD | MOTOR | NO | NA | NO | NA
1858 | IDC_Cycle_D4_Exch | 3716 | 0 | REAL | Value IDC Life Cycle | BPCS/PSD | NO | IDC | MOTOR | NO | NA | NO | NA
1859 | IDC_Hours_D4_Exch | 3720 | 0 | INT | Value IDC Hours Worked | BPCS/PSD | NO | IDC | MOTOR | NO | NA | NO | NA
1860 | PRM_Cycle_D4_Exch | 3722 | 0 | REAL | PRM Default IDC LIFE Cycle | BPCS/PSD | NO | PRM | MOTOR | NO | NA | NO | NA
1861 | PRM_Hours_D4_Exch | 3726 | 0 | INT | PRM Default IDC Hours Worked | BPCS/PSD | NO | PRM | MOTOR | NO | NA | NO | NA
1862 | Reset_IDC_D4_Exch | 3728 | 0 | BOOL | Reset IDC Values | BPCS/PSD | NO | CMD | MOTOR | NO | NA | NO | NA
1863 | APRM_Cycle_D4_Exch |  | 0 | REAL | PRM Alarmes IDC LIFE Cycle | BPCS/PSD | NO | PRM | MOTOR | NO | NA | NO | NA
1864 | APRM_Hours_D4_Exch |  | 0 | INT | PRM Alarmes IDC Hours Worked | BPCS/PSD | NO | PRM | MOTOR | NO | NA | NO | NA
1865 | Def_IDC_D4_Exch |  | 0 | BOOL | Default IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Defaut | MOTOR | NO | NA | NO | NA
1866 | Ala_IDC_D4_Exch |  | 0 | BOOL | Alarme IDC (Life cycle or Hours Worked) | BPCS/PSD | NO | Alarme | MOTOR | NO | NA | NO | NA
1867 | Def_Elec_D4_Exch |  | 0 | BOOL | Electrical Default, Please check the actuator power supply. (Disjunction) | BPCS/PSD | NO | Defaut | MOTOR | NO | NA | NO | NA
1868 | ETAT_Verrine_MarcheD1 |  | 1 | BOOL | Light Tower Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | Verrine | YES | YSI 82 | YES | YSI 42
1869 | Mode_Verrine_MarcheD1 | 3728 | 2 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | Verrine | YES | YSI 82 | YES | YSI 42
1870 | CMD_Verrine_MarcheD1 | 3728 | 3 | BOOL | Forced Value | BPCS/PSD | YES | CMD | Verrine | YES | YSI 82 | YES | YSI 42
1871 | ETAT_Verrine_MaintD1 | 3728 | 4 | BOOL | Light Tower Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | Verrine | YES | YSI 82 | YES | YSI 42
1872 | Mode_Verrine_MaintD1 | 3728 | 5 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | Verrine | YES | YSI 82 | YES | YSI 42
1873 | CMD_Verrine_maintD1 | 3728 | 6 | BOOL | Forced Value | BPCS/PSD | YES | CMD | Verrine | YES | YSI 82 | YES | YSI 42
1874 | ETAT_Verrine_MarcheD2 | 3728 | 7 | BOOL |  | BPCS/PSD | NO | Status | Verrine | NO | NA | YES | YSI 41
1875 | Mode_Verrine_MarcheD2 | 3729 | 0 | BOOL |  | BPCS/PSD | YES | CMD | Verrine | NO | NA | YES | YSI 41
1876 | CMD_Verrine_MarcheD2 | 3729 | 1 | BOOL |  | BPCS/PSD | YES | CMD | Verrine | NO | NA | YES | YSI 41
1877 | ETAT_Verrine_MaintD2 | 3729 | 2 | BOOL |  | BPCS/PSD | NO | Status | Verrine | NO | NA | YES | YSI 41
1878 | Mode_Verrine_MaintD2 | 3729 | 3 | BOOL |  | BPCS/PSD | YES | CMD | Verrine | NO | NA | YES | YSI 41
1879 | CMD_Verrine_maintD2 | 3729 | 4 | BOOL |  | BPCS/PSD | YES | CMD | Verrine | NO | NA | YES | YSI 41
1880 | ETAT_Verrine_HRSMarche | 3729 | 5 | BOOL | Light Tower Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | Verrine | YES | YSI 12 | YES | YSI 12
1881 | Mode_Verrine_HRSMarche | 3729 | 6 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | Verrine | YES | YSI 12 | YES | YSI 12
1882 | CMD_Verrine_HRSMarche | 3729 | 7 | BOOL | Forced Value | BPCS/PSD | YES | CMD | Verrine | YES | YSI 12 | YES | YSI 12
1883 | ETAT_Verrine_HRSMaint | 3730 | 0 | BOOL | Light Tower Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | Verrine | YES | YSI 12 | YES | YSI 12
1884 | Mode_Verrine_HRSMaint | 3730 | 1 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | Verrine | YES | YSI 12 | YES | YSI 12
1885 | CMD_Verrine_HRSMaint | 3730 | 2 | BOOL | Forced Value | BPCS/PSD | YES | CMD | Verrine | YES | YSI 12 | YES | YSI 12
1886 | ETAT_Autorisation_GirD1 | 3730 | 3 | BOOL |  | BPCS/PSD | NO | Status | GIR | NO | NA | NO | GIR D1
1887 | Mode_Autorisation_GirD1 | 3730 | 4 | BOOL |  | BPCS/PSD | YES | CMD | GIR | NO | NA | NO | GIR D1
1888 | CMD_Autorisation_GirD1 | 3730 | 5 | BOOL |  | BPCS/PSD | YES | CMD | GIR | NO | NA | NO | GIR D1
1889 | ETAT_Start_GirD1 | 3730 | 6 | BOOL |  | BPCS/PSD | NO | Status | GIR | NO | NA | NO | GIR D1
1890 | Mode_Start_GirD1 | 3730 | 7 | BOOL |  | BPCS/PSD | YES | CMD | GIR | NO | NA | NO | GIR D1
1891 | CMD_Start_GirD1 | 3731 | 0 | BOOL |  | BPCS/PSD | YES | CMD | GIR | NO | NA | NO | GIR D1
1892 | ETAT_Stop_GirD1 | 3731 | 1 | BOOL |  | BPCS/PSD | NO | Status | GIR | NO | NA | NO | GIR D1
1893 | Mode_Stop_GirD1 | 3731 | 2 | BOOL |  | BPCS/PSD | YES | CMD | GIR | NO | NA | NO | GIR D1
1894 | CMD_Stop_GirD1 | 3731 | 3 | BOOL |  | BPCS/PSD | YES | CMD | GIR | NO | NA | NO | GIR D1
1895 | ETAT_Autorisation_GirD2 | 3731 | 4 | BOOL |  | BPCS/PSD | NO | Status | GIR | NO | NA | NO | GIR D2
1896 | Mode_Autorisation_GirD2 | 3731 | 5 | BOOL |  | BPCS/PSD | YES | CMD | GIR | NO | NA | NO | GIR D2
1897 | CMD_Autorisation_GirD2 | 3731 | 6 | BOOL |  | BPCS/PSD | YES | CMD | GIR | NO | NA | NO | GIR D2
1898 | ETAT_Start_GirD2 | 3731 | 7 | BOOL |  | BPCS/PSD | NO | Status | GIR | NO | NA | NO | GIR D2
1899 | Mode_Start_GirD2 | 3732 | 0 | BOOL |  | BPCS/PSD | YES | CMD | GIR | NO | NA | NO | GIR D2
1900 | CMD_Start_GirD2 | 3732 | 1 | BOOL |  | BPCS/PSD | YES | CMD | GIR | NO | NA | NO | GIR D2
1901 | ETAT_Stop_GirD2 | 3732 | 2 | BOOL |  | BPCS/PSD | NO | Status | GIR | NO | NA | NO | GIR D2
1902 | Mode_Stop_GirD2 | 3732 | 3 | BOOL |  | BPCS/PSD | YES | CMD | GIR | NO | NA | NO | GIR D2
1903 | CMD_Stop_GirD2 | 3732 | 4 | BOOL |  | BPCS/PSD | YES | CMD | GIR | NO | NA | NO | GIR D2
1904 | ETAT _AutorisationD1 | 4150 | 0 | BOOL | Button Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | HS Buttons | NO | NA | NO | NA
1905 | Mode _AutorisationD1 | 4150 | 1 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | HS Buttons | NO | NA | NO | NA
1906 | CMD_AutorisationD1 | 4150 | 2 | BOOL | Forced Value | BPCS/PSD | YES | CMD | HS Buttons | NO | NA | NO | NA
1907 | ETAT _StartD1 | 4150 | 3 | BOOL | Button Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | HS Buttons | YES | HS 821 | YES | HS 421
1908 | Mode _StartD1 | 4150 | 4 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | HS Buttons | YES | HS 821 | YES | HS 421
1909 | CMD_StartD1 | 4150 | 5 | BOOL | Forced Value | BPCS/PSD | YES | CMD | HS Buttons | YES | HS 821 | YES | HS 421
1910 | ETAT _StopD1 | 4150 | 6 | BOOL | Button Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | HS Buttons | YES | HS 822 | YES | HS 422
1911 | Mode _StopD1 | 4150 | 7 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | HS Buttons | YES | HS 822 | YES | HS 422
1912 | CMD_StopD1 | 4151 | 0 | BOOL | Forced Value | BPCS/PSD | YES | CMD | HS Buttons | YES | HS 822 | YES | HS 422
1913 | ETAT _AutorisationD2 | 4151 | 1 | BOOL |  | BPCS/PSD | NO | Status | HS Buttons | NO | NA | NO | NA
1914 | Mode _AutorisationD2 | 4151 | 2 | BOOL |  | BPCS/PSD | YES | CMD | HS Buttons | NO | NA | NO | NA
1915 | CMD_AutorisationD2 | 4151 | 3 | BOOL |  | BPCS/PSD | YES | CMD | HS Buttons | NO | NA | NO | NA
1916 | ETAT _StartD2 | 4151 | 4 | BOOL |  | BPCS/PSD | NO | Status | HS Buttons | NO | NA | YES | HS 411
1917 | Mode _StartD2 | 4151 | 5 | BOOL |  | BPCS/PSD | YES | CMD | HS Buttons | NO | NA | YES | HS 411
1918 | CMD_StartD2 | 4151 | 6 | BOOL |  | BPCS/PSD | YES | CMD | HS Buttons | NO | NA | YES | HS 411
1919 | ETAT _StopD2 | 4151 | 7 | BOOL |  | BPCS/PSD | NO | Status | HS Buttons | NO | NA | YES | HS 412
1920 | Mode _StopD2 | 4152 | 0 | BOOL |  | BPCS/PSD | YES | CMD | HS Buttons | NO | NA | YES | HS 412
1921 | CMD_StopD2 | 4152 | 1 | BOOL |  | BPCS/PSD | YES | CMD | HS Buttons | NO | NA | YES | HS 412
1922 | ETAT_PSH_Comp1stHead | 4152 | 2 | BOOL | Sensor Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | PSH | NO | NA | YES | PSH 2.10
1923 | Mode_PSH_Comp1stHead | 4152 | 3 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PSH | NO | NA | YES | PSH 2.10
1924 | CMD_PSH_Comp1stHead | 4152 | 4 | BOOL | Forced Value | BPCS/PSD | YES | CMD | PSH | NO | NA | YES | PSH 2.10
1925 | ETAT_PSH_Comp2ndHead | 4152 | 5 | BOOL | Sensor Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | PSH | NO | NA | YES | PSH 2.11
1926 | Mode_PSH_Comp2ndHead | 4152 | 6 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PSH | NO | NA | YES | PSH 2.11
1927 | CMD_PSH_Comp2ndHead | 4152 | 7 | BOOL | Forced Value | BPCS/PSD | YES | CMD | PSH | NO | NA | YES | PSH 2.11
1928 | ETAT_PSL_CompH2 | 4153 | 0 | BOOL | Sensor Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | PSL | NO | NA | YES | PSL 2.12
1929 | Mode_PSL_CompH2 | 4153 | 1 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PSL | NO | NA | YES | PSL 2.12
1930 | CMD_PSL_CompH2 | 4153 | 2 | BOOL | Forced Value | BPCS/PSD | YES | CMD | PSL | NO | NA | YES | PSL 2.12
1931 | ETAT_PSL_PLATINEDep | 4153 | 3 | BOOL | Sensor Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | PSL | NO | NA | NO | NA
1932 | Mode_PSL_PLATINEDep | 4153 | 4 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | PSL | NO | NA | NO | NA
1933 | CMD_PSL_PLATINEDep | 4153 | 5 | BOOL | Forced Value | BPCS/PSD | YES | CMD | PSL | NO | NA | NO | NA
1934 | ETAT_TSL_TT_COMP_OIL | 4153 | 6 | BOOL | Sensor Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | TSL | NO | NA | YES | TSL 2.2
1935 | Mode_TSL_TT_COMP_OIL | 4153 | 7 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | TSL | NO | NA | YES | TSL 2.2
1936 | CMD_TSL_TT_COMP_OIL | 4154 | 0 | BOOL | Forced Value | BPCS/PSD | YES | CMD | TSH | NO | NA | YES | TSL 2.2
1937 | ETAT_TSH_TT_CompH2 | 4154 | 1 | BOOL | Sensor Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | TSH | NO | NA | YES | TSH 2.1
1938 | Mode_TSH_TT_CompH2 | 4154 | 2 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | TSH | NO | NA | YES | TSH 2.1
1939 | CMD_TSH_TT_CompH2 | 4154 | 3 | BOOL | Forced Value | BPCS/PSD | YES | CMD | TSH | NO | NA | YES | TSH 2.1
1940 | ETAT_TSH_Ref_CompH2 | 4154 | 4 | BOOL | Sensor Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | TSH | NO | NA | NO | NA
1941 | Mode_TSH_Ref_CompH2 | 4154 | 5 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | TSH | NO | NA | NO | NA
1942 | CMD_TSH_Ref_CompH2 | 4154 | 6 | BOOL | Forced Value | BPCS/PSD | YES | CMD | TSH | NO | NA | NO | NA
1943 | ETAT_FSL_Ref_Comp H2 | 4154 | 7 | BOOL | Sensor Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | FSL | NO | NA | YES | FSL 20.1
1944 | Mode_FSL_Ref_Comp H2 | 4155 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | FSL | NO | NA | YES | FSL 20.1
1945 | CMD_FSL_Ref_Comp H2 | 4155 | 1 | BOOL | Forced Value | BPCS/PSD | YES | CMD | FSL | NO | NA | YES | FSL 20.1
1946 | ETAT_230V_Ondule | 4155 | 2 | BOOL | Sensor Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | UPS | YES | NA | YES | NA
1947 | Mode_230V_Ondule | 4155 | 3 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | UPS | YES | NA | YES | NA
1948 | CMD_230V_Ondule | 4155 | 4 | BOOL | Forced Value | BPCS/PSD | YES | CMD | UPS | YES | NA | YES | NA
1949 | ETAT_Decro_PistoletD1 | 4155 | 5 | BOOL | Sensor Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | Pistolet | YES | NA | YES | NA
1950 | Mode_Decro_PistoletD1 | 4155 | 6 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | Pistolet | YES | NA | YES | NA
1951 | CMD_Decro_PistoletD1 | 4155 | 7 | BOOL | Forced Value | BPCS/PSD | YES | CMD | Pistolet | YES | NA | YES | NA
1952 | ETAT_Decro_PistoletD2 | 4156 | 0 | BOOL | Sensor Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | Pistolet | NO | NA | YES | NA
1953 | Mode_Decro_PistoletD2 | 4156 | 1 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | Pistolet | NO | NA | YES | NA
1954 | CMD_Decro_PistoletD2 | 4156 | 2 | BOOL | Forced Value | BPCS/PSD | YES | CMD | Pistolet | NO | NA | YES | NA
1955 | ETAT_XHS_VibrationD1 | 4156 | 3 | BOOL |  | BPCS/PSD | NO | Status | XHS | NO | NA | NO | NA
1956 | Mode_XHS_VibrationD1 | 4156 | 4 | BOOL |  | BPCS/PSD | YES | CMD | XHS | NO | NA | NO | NA
1957 | CMD_XHS_VibrationD1 | 4156 | 5 | BOOL |  | BPCS/PSD | YES | CMD | XHS | NO | NA | NO | NA
1958 | ETAT_XHS_VibrationD2 | 4156 | 6 | BOOL |  | BPCS/PSD | NO | Status | XHS | NO | NA | NO | NA
1959 | Mode_XHS_VibrationD2 | 4156 | 7 | BOOL |  | BPCS/PSD | YES | CMD | XHS | NO | NA | NO | NA
1960 | CMD_XHS_VibrationD2 | 4157 | 0 | BOOL |  | BPCS/PSD | YES | CMD | XHS | NO | NA | NO | NA
1961 | ETAT_Disjon_ExchD1 | 4157 | 1 | BOOL | Disjoncteur Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | Circuit Breaker | YES | E 8.201 | YES | R 40
1962 | Mode_Disjon_ExchD1 | 4157 | 2 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | Circuit Breaker | YES | E 8.201 | YES | R 40
1963 | CMD_Disjon_ExchD1 | 4157 | 3 | BOOL | Forced Value | BPCS/PSD | YES | CMD | Circuit Breaker | YES | E 8.201 | YES | R 40
1964 | ETAT_Disjon_ExchD2 | 4157 | 4 | BOOL |  | BPCS/PSD | NO | Status | Circuit Breaker | NO | NA | NO | NA
1965 | Mode_Disjon_ExchD2 | 4157 | 5 | BOOL |  | BPCS/PSD | YES | CMD | Circuit Breaker | NO | NA | NO | NA
1966 | CMD_Disjon_ExchD2 | 4157 | 6 | BOOL |  | BPCS/PSD | YES | CMD | Circuit Breaker | NO | NA | NO | NA
1967 | ETAT_Disjon_AirExtract | 4157 | 7 | BOOL | Disjoncteur Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | Circuit Breaker | YES | C 121/122 | YES | C 21
1968 | Mode_Disjon_AirExtract | 4158 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | Circuit Breaker | YES | C 121/122 | YES | C 21
1969 | CMD_Disjon_AirExtract | 4158 | 1 | BOOL | Forced Value | BPCS/PSD | YES | CMD | Circuit Breaker | YES | C 121/122 | YES | C 21
1970 | ETAT_Disjon_AirComp | 4158 | 2 | BOOL | Disjoncteur Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | Circuit Breaker | YES | C12.1 | YES | C 12.1 / C 12.2
1971 | Mode_Disjon_AirComp | 4158 | 3 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | Circuit Breaker | YES | C12.1 | YES | C 12.1 / C 12.2
1972 | CMD_Disjon_AirComp | 4158 | 4 | BOOL | Forced Value | BPCS/PSD | YES | CMD | Circuit Breaker | YES | C12.1 | YES | C 12.1 / C 12.2
1973 | ETAT_RMEP_AirExtract | 4158 | 5 | BOOL | RMEP Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | MOTOR | YES | C 121/122 | YES | C 21
1974 | Mode_RMEP_AirExtract | 4158 | 6 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | MOTOR | YES | C 121/122 | YES | C 21
1975 | CMD_RMEP_AirExtract | 4158 | 7 | BOOL | Forced Value | BPCS/PSD | YES | CMD | MOTOR | YES | C 121/122 | YES | C 21
1976 | ETAT_RMEP_AirComp | 4159 | 0 | BOOL | RMEP Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | MOTOR | YES | C12.1 | YES | C 12.1 / C 12.2
1977 | Mode_RMEP_AirComp | 4159 | 1 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | MOTOR | YES | C12.1 | YES | C 12.1 / C 12.2
1978 | CMD_RMEP_AirComp | 4159 | 2 | BOOL | Forced Value | BPCS/PSD | YES | CMD | MOTOR | YES | C12.1 | YES | C 12.1 / C 12.2
1979 | ETAT_Disjon_CompH2 | 4159 | 3 | BOOL | RMEP Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | Circuit Breaker | NO | NA | YES | C2
1980 | Mode_Disjon_CompH2 | 4159 | 4 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | Circuit Breaker | NO | NA | YES | C2
1981 | CMD_Disjon_CompH2 | 4159 | 5 | BOOL | Forced Value | BPCS/PSD | YES | CMD | Circuit Breaker | NO | NA | YES | C2
1982 | ETAT_Disjon_RefCompH2 | 4159 | 6 | BOOL | RMEP Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | Circuit Breaker | NO | NA | YES | R20
1983 | Mode_Disjon_RefCompH2 | 4159 | 7 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | Circuit Breaker | NO | NA | YES | R20
1984 | CMD_Disjon_RefCompH2 | 4160 | 0 | BOOL | Forced Value | BPCS/PSD | YES | CMD | Circuit Breaker | NO | NA | YES | R20
1985 | ETAT_DemarrCompH2OK | 4160 | 1 | BOOL | Demarreur OK Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | MOTOR | NO | NA | YES | Soft Starter Motor
1986 | Mode_DemarrCompH2OK | 4160 | 2 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | MOTOR | NO | NA | YES | Soft Starter Motor
1987 | CMD_DemarrCompH2OK | 4160 | 3 | BOOL | Forced Value | BPCS/PSD | YES | CMD | MOTOR | NO | NA | YES | Soft Starter Motor
1988 | ETAT_DemarrCompH2Def | 4160 | 4 | BOOL | Demarreur Default Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | MOTOR | NO | NA | YES | Soft Starter Motor
1989 | Mode_DemarrCompH2Def | 4160 | 5 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | MOTOR | NO | NA | YES | Soft Starter Motor
1990 | CMD_DemarrCompH2Def | 4160 | 6 | BOOL | Forced Value | BPCS/PSD | YES | CMD | MOTOR | NO | NA | YES | Soft Starter Motor
1991 | ETAT_FSL_Ventil_Comp | 4160 | 7 | BOOL | Sensor Status 1 = ON, 0= OFF | BPCS/PSD | NO | Status | FSL | NO | NA | YES | FSL 21
1992 | Mode_FSL_Ventil_Comp | 4161 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | FSL | NO | NA | YES | FSL 21
1993 | CMD_FSL_Ventil_Comp | 4161 | 1 | BOOL | Forced Value | BPCS/PSD | YES | CMD | FSL | NO | NA | YES | FSL 21
1994 | ETAT_SIF_11_2H | 4161 | 2 | BOOL |  | BPCS/PSD | NO | Status | SIS | YES | NA | NO | NA
1995 | ETAT_SRS_SIF_21_2H | 4161 | 3 | BOOL |  | BPCS/PSD | NO | Status | SIS | YES | NA | NO | NA
1996 | ETAT_SRS_SIF_22_2H | 4161 | 4 | BOOL |  | BPCS/PSD | NO | Status | SIS | YES | NA | NO | NA
1997 | ETAT_SRS_SIF_23_1H | 4161 | 5 | BOOL |  | BPCS/PSD | NO | Status | SIS | YES | NA | NO | NA
1998 | ETAT_SRS_SIF_23_2H | 4161 | 6 | BOOL |  | BPCS/PSD | NO | Status | SIS | YES | NA | NO | NA
1999 | ETAT_SRS_SIF_24_1H | 4161 | 7 | BOOL |  | BPCS/PSD | NO | Status | SIS | YES | NA | NO | NA
2000 | ETAT_SRS_SIF_4101_1H | 4162 | 0 | BOOL |  | BPCS/PSD | NO | Status | SIS | YES | NA | NO | NA
2001 | ETAT_SRS_SIF_8201_1H | 4162 | 1 | BOOL |  | BPCS/PSD | NO | Status | SIS | YES | NA | NO | NA
2002 | ETAT_SRS_SIF_8201_1L | 4162 | 2 | BOOL |  | BPCS/PSD | NO | Status | SIS | YES | NA | NO | NA
2003 | ETAT_ALLSIS | 4162 | 3 | BOOL | Global Status Function SIS , 1= Ok , 0= NonOK | BPCS/PSD | NO | Status | SIS | YES | NA | NO | NA
2004 | BP_ACQ_PSD_Comp | 4178 | 0 | BOOL | Button ACQ Zone Compression | BPCS/PSD | NO | CMD | Acknowledgement | YES | NA | YES | Acknowledge
2005 | BP_ACQ_PSD_Common | 4178 | 1 | BOOL | Button ACQ Zone Common | BPCS/PSD | NO | CMD | Acknowledgement | YES | NA | YES | Acknowledge
2006 | BP_ACQ_PSD_Hardware | 4178 | 2 | BOOL | Button ACQ Hardware Default | BPCS/PSD | NO | CMD | Acknowledgement | YES | NA | YES | Acknowledge
2007 | BP_ACQ_PSD_D1 | 4178 | 3 | BOOL | Button ACQ Zone D1 | BPCS/PSD | NO | CMD | Acknowledgement | YES | NA | YES | Acknowledge
2008 | BP_ACQ_PSD_D2 | 4178 | 4 | BOOL | Button ACQ Zone D2 | BPCS/PSD | NO | CMD | Acknowledgement | NO | NA | YES | Acknowledge
2009 | BP_ACQ_PSD_D3 | 4178 | 5 | BOOL | Button ACQ Zone D3 | BPCS/PSD | NO | CMD | Acknowledgement | NO | NA | NO | NA
2010 | BP_ACQ_PSD_D4 | 4178 | 6 | BOOL | Button ACQ Zone D4 | BPCS/PSD | NO | CMD | Acknowledgement | NO | NA | NO | NA
2011 | BP_ACQ_Info | 4187 | 6 | BOOL | Button ACQ INFO | BPCS/PSD | NO | CMD | Acknowledgement | YES | NA | YES | Acknowledge
2012 | BP_CMD_ArretCompNorm | 4178 | 7 | BOOL | Button CMD Arrete Compression Normal | BPCS/PSD | NO | CMD | HMI CMD | YES | NA | YES | NA
2013 | BP_CMD_ArretComp | 4179 | 0 | BOOL | Button CMD Arrete Compression | BPCS/PSD | NO | CMD | HMI CMD | YES | NA | YES | NA
2014 | BP_CMD_SignalTechni | 4179 | 1 | BOOL | Button CMD Signal Technicien | BPCS/PSD | NO | CMD | HMI CMD | YES | NA | YES | NA
2015 | RAZ_Stk_STK10 | 4183 | 5 | BOOL | Button Reset Indicators Stockage 10 | BPCS/PSD | NO | CMD | HMI CMD | YES | STK 1.1 | YES | STK 1.1
2016 | RAZ_Stk_STK11 | 4183 | 6 | BOOL | Button Reset Indicators Stockage 11 | BPCS/PSD | NO | CMD | HMI CMD | YES | STK 7.1 | YES | STK 3.1
2017 | RAZ_Stk_STK12 | 4183 | 7 | BOOL | Button Reset Indicators Stockage 12 | BPCS/PSD | NO | CMD | HMI CMD | YES | STK 7.2 | YES | STK 3.2
2018 | RAZ_Stk_STK13 | 4184 | 0 | BOOL | Button Reset Indicators Stockage 13 | BPCS/PSD | NO | CMD | HMI CMD | YES | STK 7.3 | YES | STK 3.3
2019 | RAZ_Stk_STK14 | 4184 | 1 | BOOL |  | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | YES | STK 3.4
2020 | RAZ_Stk_STK15 | 4184 | 2 | BOOL |  | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | NO | NA
2021 | RAZ_Stk_STK16 | 4184 | 3 | BOOL |  | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | NO | NA
2022 | RAZ_Stk_STK17 | 4184 | 4 | BOOL |  | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | NO | NA
2023 | RAZ_Stk_STK18 | 4184 | 5 | BOOL |  | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | NO | NA
2024 | RAZ_Stk_STK19 | 4184 | 6 | BOOL |  | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | NO | NA
2025 | RAZ_Stk_STK20 | 4184 | 7 | BOOL |  | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | NO | NA
2026 | STK_Dispo_STK10 | 4185 | 0 | BOOL | Button Stockage 10 Maint to Dispo | BPCS/PSD | NO | CMD | HMI CMD | YES | STK 1.1 | YES | STK 1.1
2027 | STK_Dispo_STK11 | 4185 | 1 | BOOL | Button Stockage 11 Maint to Dispo | BPCS/PSD | NO | CMD | HMI CMD | YES | STK 7.1 | YES | STK 3.1
2028 | STK_Dispo_STK12 | 4185 | 2 | BOOL | Button Stockage 12 Maint to Dispo | BPCS/PSD | NO | CMD | HMI CMD | YES | STK 7.2 | YES | STK 3.2
2029 | STK_Dispo_STK13 | 4185 | 3 | BOOL | Button Stockage 13 Maint to Dispo | BPCS/PSD | NO | CMD | HMI CMD | YES | STK 7.3 | YES | STK 3.3
2030 | STK_Dispo_STK14 | 4185 | 4 | BOOL |  | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | YES | STK 3.4
2031 | STK_Dispo_STK15 | 4185 | 5 | BOOL |  | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | NO | NA
2032 | STK_Dispo_STK16 | 4185 | 6 | BOOL |  | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | NO | NA
2033 | STK_Dispo_STK17 | 4185 | 7 | BOOL |  | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | NO | NA
2034 | STK_Dispo_STK18 | 4186 | 0 | BOOL |  | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | NO | NA
2035 | STK_Dispo_STK19 | 4186 | 1 | BOOL |  | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | NO | NA
2036 | STK_Dispo_STK20 | 4186 | 2 | BOOL |  | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | NO | NA
2037 | STK_Maint_STK10 | 4186 | 3 | BOOL | Button Stockage 10 Dispo to Maint | BPCS/PSD | NO | CMD | HMI CMD | YES | STK 1.1 | YES | STK 1.1
2038 | STK_Maint_STK11 | 4186 | 4 | BOOL | Button Stockage 11 Dispo to Maint | BPCS/PSD | NO | CMD | HMI CMD | YES | STK 7.1 | YES | STK 3.1
2039 | STK_Maint_STK12 | 4186 | 5 | BOOL | Button Stockage 12 Dispo to Maint | BPCS/PSD | NO | CMD | HMI CMD | YES | STK 7.2 | YES | STK 3.2
2040 | STK_Maint_STK13 | 4186 | 6 | BOOL | Button Stockage 13 Dispo to Maint | BPCS/PSD | NO | CMD | HMI CMD | YES | STK 7.3 | YES | STK 3.3
2041 | STK_Maint_STK14 | 4186 | 7 | BOOL | Button Stockage 14 Dispo to Maint | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | YES | STK 3.4
2042 | STK_Maint_STK15 | 4187 | 0 | BOOL | Button Stockage 15 Dispo to Maint | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | NO | NA
2043 | STK_Maint_STK16 | 4187 | 1 | BOOL | Button Stockage 16 Dispo to Maint | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | NO | NA
2044 | STK_Maint_STK17 | 4187 | 2 | BOOL | Button Stockage 17 Dispo to Maint | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | NO | NA
2045 | STK_Maint_STK18 | 4187 | 3 | BOOL | Button Stockage 18 Dispo to Maint | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | NO | NA
2046 | STK_Maint_STK19 | 4187 | 4 | BOOL | Button Stockage 19 Dispo to Maint | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | NO | NA
2047 | STK_Maint_STK20 | 4187 | 5 | BOOL | Button Stockage 20 Dispo to Maint | BPCS/PSD | NO | CMD | HMI CMD | NO | NA | NO | NA
2048 | MES_XHS_ACCEL_D1 | 4188 | 0 | REAL |  | BPCS/PSD | NO | Measure | XHS | YES | XSH82 | YES | XSH 42
2049 | ScaleMIN_XHS_ACCEL_D1 | 4192 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | XHS | YES | XSH82 | YES | XSH 42
2050 | ScaleMAX_XHS_ACCEL_D1 | 4196 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | XHS | YES | XSH82 | YES | XSH 42
2051 | ModeSimu_XHS_ACCEL_D1 | 4200 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | XHS | YES | XSH82 | YES | XSH 42
2052 | CMDSimu_XHS_ACCEL_D1 | 4202 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | XHS | YES | XSH82 | YES | XSH 42
2053 | ActPSDSL_XHS_ACCEL_D1 | 4206 | 0 | BOOL | PRM ON/OFF Seuil L | BPCS/PSD | NO | PRM | XHS | YES | XSH82 | YES | XSH 42
2054 | PSDSL_XHS_ACCEL_D1 | 4208 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | XHS | YES | XSH82 | YES | XSH 42
2055 | ActPSDSH_XHS_ACCEL_D1 | 4212 | 0 | BOOL | PRM ON/OFF Seuil H | BPCS/PSD | NO | PRM | XHS | YES | XSH82 | YES | XSH 42
2056 | PSDSH_XHS_ACCEL_D1 | 4214 | 0 | REAL | PRM Seuil PSD H | BPCS/PSD | NO | PRM | XHS | YES | XSH82 | YES | XSH 42
2057 | Type_XHS_ACCEL_D1 | 4218 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | XHS | YES | XSH82 | YES | XSH 42
2058 | Cha_Def_XHS_ACCEL_D1 | 4252 | 0 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | XHS | YES | XSH82 | YES | XSH 42
2059 | MES_XHS_ACCEL_D2 | 4220 | 0 | REAL |  | BPCS/PSD | NO | Measure | XHS | NO | NA | YES | XHS 41
2060 | ScaleMIN_XHS_ACCEL_D2 | 4224 | 0 | REAL |  | BPCS/PSD | NO | PRM | XHS | NO | NA | YES | XHS 41
2061 | ScaleMAX_XHS_ACCEL_D2 | 4228 | 0 | REAL |  | BPCS/PSD | NO | PRM | XHS | NO | NA | YES | XHS 41
2062 | ModeSimu_XHS_ACCEL_D2 | 4232 | 0 | BOOL |  | BPCS/PSD | YES | CMD | XHS | NO | NA | YES | XHS 41
2063 | CMDSimu_XHS_ACCEL_D2 | 4234 | 0 | REAL |  | BPCS/PSD | YES | CMD | XHS | NO | NA | YES | XHS 41
2064 | ActPSDSL_XHS_ACCEL_D2 | 4238 | 0 | BOOL |  | BPCS/PSD | NO | PRM | XHS | NO | NA | YES | XHS 41
2065 | PSDSL_XHS_ACCEL_D2 | 4240 | 0 | REAL |  | BPCS/PSD | NO | PRM | XHS | NO | NA | YES | XHS 41
2066 | ActPSDSH_XHS_ACCEL_D2 | 4244 | 0 | BOOL |  | BPCS/PSD | NO | PRM | XHS | NO | NA | YES | XHS 41
2067 | PSDSH_XHS_ACCEL_D2 | 4246 | 0 | REAL |  | BPCS/PSD | NO | PRM | XHS | NO | NA | YES | XHS 41
2068 | Type_XHS_ACCEL_D2 | 4250 | 0 | INT |  | BPCS/PSD | NO | PRM | XHS | NO | NA | YES | XHS 41
2069 | Cha_Def_XHS_ACCEL_D2 | 4252 | 1 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | XHS | NO | NA | YES | XHS 41
2070 | Alarm_STK1 | 4715 | 0 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2071 | Alarm_STK2 | 4715 | 1 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2072 | Alarm_STK3 | 4715 | 2 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2073 | Alarm_STK4 | 4715 | 3 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2074 | Alarm_STK5 | 4715 | 4 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2075 | Alarm_STK6 | 4715 | 5 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2076 | Alarm_STK7 | 4715 | 6 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2077 | Alarm_STK8 | 4715 | 7 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2078 | Alarm_STK9 | 4716 | 0 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2079 | Alarm_STK10 | 4716 | 1 | BOOL | Warning! "Storage 1 LP" Number of cycles too High. | BPCS/PSD | NO | Alarme | Stockage | YES | STK 1.1 | YES | STK 1.1
2080 | Alarm_STK11 | 4716 | 2 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | YES | STK 3.1
2081 | Alarm_STK12 | 4716 | 3 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | YES | STK 3.2
2082 | Alarm_STK13 | 4716 | 4 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | YES | STK 3.3
2083 | Alarm_STK14 | 4716 | 5 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | YES | STK 3.4
2084 | Alarm_STK15 | 4716 | 6 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2085 | Alarm_STK16 | 4716 | 7 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2086 | Alarm_STK17 | 4717 | 0 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2087 | Alarm_STK18 | 4717 | 1 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2088 | Alarm_STK19 | 4717 | 2 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2089 | Alarm_STK20 | 4717 | 3 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2090 | Alarm_STK21 | 4717 | 4 | BOOL | Warning! "Storage 1 HP" Number of cycles too High. | BPCS/PSD | NO | Alarme | Stockage | YES | STK 7.1 | NO | NA
2091 | Alarm_STK22 | 4717 | 5 | BOOL | Warning! "Storage 2 HP" Number of cycles too High. | BPCS/PSD | NO | Alarme | Stockage | YES | STK 7.2 | NO | NA
2092 | Alarm_STK23 | 4717 | 6 | BOOL | Warning! "Storage 3 HP" Number of cycles too High. | BPCS/PSD | NO | Alarme | Stockage | YES | STK 7.3 | NO | NA
2093 | Alarm_STK24 | 4717 | 7 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2094 | Alarm_STK25 | 4718 | 0 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2095 | Alarm_STK26 | 4718 | 1 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2096 | Alarm_STK27 | 4718 | 2 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2097 | Alarm_STK28 | 4718 | 3 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2098 | Alarm_STK29 | 4718 | 4 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2099 | Alarm_STK30 | 4718 | 5 | BOOL |  | BPCS/PSD | NO | Alarme | Stockage | NO | NA | NO | NA
2100 | Default_STK1 | 4718 | 6 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2101 | Default_STK2 | 4718 | 7 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2102 | Default_STK3 | 4719 | 0 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2103 | Default_STK4 | 4719 | 1 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2104 | Default_STK5 | 4719 | 2 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2105 | Default_STK6 | 4719 | 3 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2106 | Default_STK7 | 4719 | 4 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2107 | Default_STK8 | 4719 | 5 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2108 | Default_STK9 | 4719 | 6 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2109 | Default_STK10 | 4719 | 7 | BOOL | Default! "Storage 1 LP" Number of cycles too High. | BPCS/PSD | NO | Defaut | Stockage | YES | STK 1.1 | YES | STK 1.1
2110 | Default_STK11 | 4720 | 0 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | YES | STK 3.1
2111 | Default_STK12 | 4720 | 1 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | YES | STK 3.2
2112 | Default_STK13 | 4720 | 2 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | YES | STK 3.3
2113 | Default_STK14 | 4720 | 3 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | YES | STK 3.4
2114 | Default_STK15 | 4720 | 4 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2115 | Default_STK16 | 4720 | 5 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2116 | Default_STK17 | 4720 | 6 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2117 | Default_STK18 | 4720 | 7 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2118 | Default_STK19 | 4721 | 0 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2119 | Default_STK20 | 4721 | 1 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2120 | Default_STK21 | 4721 | 2 | BOOL | Default! "Storage 1 HP" Number of cycles too High. | BPCS/PSD | NO | Defaut | Stockage | YES | STK 7.1 | NO | NA
2121 | Default_STK22 | 4721 | 3 | BOOL | Default! "Storage 3 HP" Number of cycles too High. | BPCS/PSD | NO | Defaut | Stockage | YES | STK 7.2 | NO | NA
2122 | Default_STK23 | 4721 | 4 | BOOL | Default! "Storage 3 HP" Number of cycles too High. | BPCS/PSD | NO | Defaut | Stockage | YES | STK 7.3 | NO | NA
2123 | Default_STK24 | 4721 | 5 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2124 | Default_STK25 | 4721 | 6 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2125 | Default_STK26 | 4721 | 7 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2126 | Default_STK27 | 4722 | 0 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2127 | Default_STK28 | 4722 | 1 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2128 | Default_STK29 | 4722 | 2 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2129 | Default_STK30 | 4722 | 3 | BOOL |  | BPCS/PSD | NO | Defaut | Stockage | NO | NA | NO | NA
2130 | HRSVariante_ResBOOL1 | 4714 | 7 | BOOL | Button ByPASS Compensation SYSTEM (H2M) | BPCS/PSD | NO | CMD | HMI CMD | YES | NA | NO | NA
2131 | HRSVariante_ResBOOL2 | 5172 | 1 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2132 | HRSVariante_ResBOOL3 | 5172 | 2 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2133 | HRSVariante_ResBOOL4 | 5172 | 3 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2134 | HRSVariante_ResBOOL5 | 5172 | 4 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2135 | HRSVariante_ResBOOL6 | 5172 | 5 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2136 | HRSVariante_ResBOOL7 | 5172 | 6 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2137 | HRSVariante_ResBOOL8 | 5172 | 7 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2138 | HRSVariante_ResBOOL9 | 5173 | 0 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2139 | HRSVariante_ResBOOL10 | 5173 | 1 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2140 | HRSVariante_ResBOOL11 | 5173 | 2 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2141 | HRSVariante_ResBOOL12 | 5173 | 3 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2142 | HRSVariante_ResBOOL13 | 5173 | 4 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2143 | HRSVariante_ResBOOL14 | 5173 | 5 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2144 | HRSVariante_ResBOOL15 | 5173 | 6 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2145 | HRSVariante_ResBOOL16 | 5173 | 7 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2146 | HRSVariante_ResBOOL17 | 5174 | 0 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2147 | HRSVariante_ResBOOL18 | 5174 | 1 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2148 | HRSVariante_ResBOOL19 | 5174 | 2 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2149 | HRSVariante_ResBOOL20 | 5174 | 3 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2150 | HRSVariante_ResBOOL21 | 5174 | 4 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2151 | HRSVariante_ResBOOL22 | 5174 | 5 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2152 | HRSVariante_ResBOOL23 | 5174 | 6 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2153 | HRSVariante_ResBOOL24 | 5174 | 7 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2154 | HRSVariante_ResBOOL25 | 5175 | 0 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2155 | HRSVariante_ResBOOL26 | 5175 | 1 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2156 | HRSVariante_ResBOOL27 | 5175 | 2 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2157 | HRSVariante_ResBOOL28 | 5175 | 3 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2158 | HRSVariante_ResBOOL29 | 5175 | 4 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2159 | HRSVariante_ResBOOL30 | 5175 | 5 | BOOL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2160 | PRMAlarm_Cycle_STK1 | 4724 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2161 | PRMAlarm_Cycle_STK2 | 4728 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2162 | PRMAlarm_Cycle_STK3 | 4732 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2163 | PRMAlarm_Cycle_STK4 | 4736 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2164 | PRMAlarm_Cycle_STK5 | 4740 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2165 | PRMAlarm_Cycle_STK6 | 4744 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2166 | PRMAlarm_Cycle_STK7 | 4748 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2167 | PRMAlarm_Cycle_STK8 | 4752 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2168 | PRMAlarm_Cycle_STK9 | 4756 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2169 | PRMAlarm_Cycle_STK10 | 4760 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | YES | STK 1.1 | YES | STK 1.1
2170 | PRMAlarm_Cycle_STK11 | 4764 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | YES | STK 3.1
2171 | PRMAlarm_Cycle_STK12 | 4768 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | YES | STK 3.2
2172 | PRMAlarm_Cycle_STK13 | 4772 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | YES | STK 3.3
2173 | PRMAlarm_Cycle_STK14 | 4776 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | YES | STK 3.4
2174 | PRMAlarm_Cycle_STK15 | 4780 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2175 | PRMAlarm_Cycle_STK16 | 4784 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2176 | PRMAlarm_Cycle_STK17 | 4788 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2177 | PRMAlarm_Cycle_STK18 | 4792 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2178 | PRMAlarm_Cycle_STK19 | 4796 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2179 | PRMAlarm_Cycle_STK20 | 4800 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2180 | PRMAlarm_Cycle_STK21 | 4804 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | YES | STK 7.1 | NO | NA
2181 | PRMAlarm_Cycle_STK22 | 4808 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | YES | STK 7.2 | NO | NA
2182 | PRMAlarm_Cycle_STK23 | 4812 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | YES | STK 7.3 | NO | NA
2183 | PRMAlarm_Cycle_STK24 | 4816 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2184 | PRMAlarm_Cycle_STK25 | 4820 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2185 | PRMAlarm_Cycle_STK26 | 4824 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2186 | PRMAlarm_Cycle_STK27 | 4828 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2187 | PRMAlarm_Cycle_STK28 | 4832 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2188 | PRMAlarm_Cycle_STK29 | 4836 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2189 | PRMAlarm_Cycle_STK30 | 4840 | 0 | REAL | PRM Alarm Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2190 | PRMDef_Cycle_STK1 | 4844 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2191 | PRMDef_Cycle_STK2 | 4848 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2192 | PRMDef_Cycle_STK3 | 4852 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2193 | PRMDef_Cycle_STK4 | 4856 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2194 | PRMDef_Cycle_STK5 | 4860 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2195 | PRMDef_Cycle_STK6 | 4864 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2196 | PRMDef_Cycle_STK7 | 4868 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2197 | PRMDef_Cycle_STK8 | 4872 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2198 | PRMDef_Cycle_STK9 | 4876 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2199 | PRMDef_Cycle_STK10 | 4880 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | YES | STK 1.1 | YES | STK 1.1
2200 | PRMDef_Cycle_STK11 | 4884 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | YES | STK 3.1
2201 | PRMDef_Cycle_STK12 | 4888 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | YES | STK 3.2
2202 | PRMDef_Cycle_STK13 | 4892 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | YES | STK 3.3
2203 | PRMDef_Cycle_STK14 | 4896 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | YES | STK 3.4
2204 | PRMDef_Cycle_STK15 | 4900 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2205 | PRMDef_Cycle_STK16 | 4904 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2206 | PRMDef_Cycle_STK17 | 4908 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2207 | PRMDef_Cycle_STK18 | 4912 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2208 | PRMDef_Cycle_STK19 | 4916 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2209 | PRMDef_Cycle_STK20 | 4920 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2210 | PRMDef_Cycle_STK21 | 4924 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | YES | STK 7.1 | NO | NA
2211 | PRMDef_Cycle_STK22 | 4928 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | YES | STK 7.2 | NO | NA
2212 | PRMDef_Cycle_STK23 | 4932 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | YES | STK 7.3 | NO | NA
2213 | PRMDef_Cycle_STK24 | 4936 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2214 | PRMDef_Cycle_STK25 | 4940 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2215 | PRMDef_Cycle_STK26 | 4944 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2216 | PRMDef_Cycle_STK27 | 4948 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2217 | PRMDef_Cycle_STK28 | 4952 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2218 | PRMDef_Cycle_STK29 | 4956 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2219 | PRMDef_Cycle_STK30 | 4960 | 0 | REAL | PRM Def Cycles Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2220 | MES_SANAPTAVAL_D1 | 4964 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | Compensation | YES | NA | NO | NA
2221 | ScaleMIN_SANAPTAVALD1 | 4968 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | Compensation | YES | NA | NO | NA
2222 | ScaleMAX_SANAPTAVALD1 | 4972 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | Compensation | YES | NA | NO | NA
2223 | ModeSimu_SANAPTAVALD1 | 4976 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | Compensation | YES | NA | NO | NA
2224 | CMDSimu_SANAPTAVALD1 | 4978 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | Compensation | YES | NA | NO | NA
2225 | Type_SANAPTAVALD1 | 4982 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | Compensation | YES | NA | NO | NA
2226 | Cha_Def_SANAPTAVALD1 | 4984 | 0 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | Compensation | YES | NA | NO | NA
2227 | MES_SANATTAVALD1 | 4986 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | Compensation | YES | NA | NO | NA
2228 | ScaleMIN_SANATTAVALD1 | 4990 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | Compensation | YES | NA | NO | NA
2229 | ScaleMAX_SANATTAVALD1 | 4994 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | Compensation | YES | NA | NO | NA
2230 | ModeSimu_SANATTAVALD1 | 4998 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | Compensation | YES | NA | NO | NA
2231 | CMDSimu_SANATTAVALD1 | 5000 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | Compensation | YES | NA | NO | NA
2232 | Type_SANATTAVALD1 | 5004 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | Compensation | YES | NA | NO | NA
2233 | Cha_Def_SANATTAVALD1 | 5006 | 0 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | Compensation | YES | NA | NO | NA
2234 | ETAT_Compens_OKD1 | 5006 | 1 | BOOL | Status Input Mot de Vie Compensation system | BPCS/PSD | NO | Status | Compensation | YES | NA | NO | NA
2235 | Mode_Compens_OKD1 | 5006 | 2 | BOOL | Mode Input Mot de Vie Compensation system | BPCS/PSD | YES | CMD | Compensation | YES | NA | NO | NA
2236 | CMD_Compens_OKD1 | 5006 | 3 | BOOL | CMD Input Mot de Vie Compensation system | BPCS/PSD | YES | CMD | Compensation | YES | NA | NO | NA
2237 | ETAT_Author_CompensD1 | 5006 | 4 | BOOL | Status Output Author_Compens Compensation system (Start Calculator) | BPCS/PSD | NO | Status | Compensation | YES | NA | NO | NA
2238 | Mode_Author_CompensD1 | 5006 | 5 | BOOL | Mode Output Author_Compens Compensation system | BPCS/PSD | YES | CMD | Compensation | YES | NA | NO | NA
2239 | CMD_Author_CompensD1 | 5006 | 6 | BOOL | CMD Output Author_Compens Compensation system | BPCS/PSD | YES | CMD | Compensation | YES | NA | NO | NA
2240 | MES_SANAPTAVAL_D2 | 5008 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | Compensation | NO | NA | NO | NA
2241 | ScaleMIN_SANAPTAVALD2 | 5012 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | Compensation | NO | NA | NO | NA
2242 | ScaleMAX_SANAPTAVALD2 | 5016 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | Compensation | NO | NA | NO | NA
2243 | ModeSimu_SANAPTAVALD2 | 5020 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | Compensation | NO | NA | NO | NA
2244 | CMDSimu_SANAPTAVALD2 | 5022 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | Compensation | NO | NA | NO | NA
2245 | Type_SANAPTAVALD2 | 5026 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | Compensation | NO | NA | NO | NA
2246 | Cha_Def_SANAPTAVALD2 | 5028 | 0 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | Compensation | NO | NA | NO | NA
2247 | MES_SANATTAVALD2 | 5030 | 0 | REAL | Sensor Measurement | BPCS/PSD | NO | Measure | Compensation | NO | NA | NO | NA
2248 | ScaleMIN_SANATTAVALD2 | 5034 | 0 | REAL | PRM Echelle MIN | BPCS/PSD | NO | PRM | Compensation | NO | NA | NO | NA
2249 | ScaleMAX_SANATTAVALD2 | 5038 | 0 | REAL | PRM Echelle MAX | BPCS/PSD | NO | PRM | Compensation | NO | NA | NO | NA
2250 | ModeSimu_SANATTAVALD2 | 5042 | 0 | BOOL | ON/OFF Forced Value | BPCS/PSD | YES | CMD | Compensation | NO | NA | NO | NA
2251 | CMDSimu_SANATTAVALD2 | 5044 | 0 | REAL | Forced Value | BPCS/PSD | YES | CMD | Compensation | NO | NA | NO | NA
2252 | Type_SANATTAVALD2 | 5048 | 0 | INT | PRM Sensor Type | BPCS/PSD | NO | PRM | Compensation | NO | NA | NO | NA
2253 | Cha_Def_SANATTAVALD2 | 5050 | 0 | BOOL | Sensor Channel Default. Please check the Sensor Wiring. | BPCS/PSD | NO | Defaut | Compensation | NO | NA | NO | NA
2254 | ETAT_Compens_OKD2 | 5050 | 1 | BOOL | Status Input Mot de Vie Compensation system | BPCS/PSD | NO | Status | Compensation | NO | NA | NO | NA
2255 | Mode_Compens_OKD2 | 5050 | 2 | BOOL | Mode Input Mot de Vie Compensation system | BPCS/PSD | YES | CMD | Compensation | NO | NA | NO | NA
2256 | CMD_Compens_OKD2 | 5050 | 3 | BOOL | CMD Input Mot de Vie Compensation system | BPCS/PSD | YES | CMD | Compensation | NO | NA | NO | NA
2257 | ETAT_Author_CompensD2 | 5050 | 4 | BOOL | Status Output Author_Compens Compensation system | BPCS/PSD | NO | Status | Compensation | NO | NA | NO | NA
2258 | Mode_Author_CompensD2 | 5050 | 5 | BOOL | Mode Output Author_Compens Compensation system | BPCS/PSD | YES | CMD | Compensation | NO | NA | NO | NA
2259 | CMD_Author_CompensD2 | 5050 | 6 | BOOL | CMD Output Author_Compens Compensation system | BPCS/PSD | YES | CMD | Compensation | NO | NA | NO | NA
2260 | PRMAlarm_Hour_STK1 | 5052 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2261 | PRMAlarm_Hour_STK2 | 5054 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2262 | PRMAlarm_Hour_STK3 | 5056 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2263 | PRMAlarm_Hour_STK4 | 5058 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2264 | PRMAlarm_Hour_STK5 | 5060 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2265 | PRMAlarm_Hour_STK6 | 5062 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2266 | PRMAlarm_Hour_STK7 | 5064 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2267 | PRMAlarm_Hour_STK8 | 5066 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2268 | PRMAlarm_Hour_STK9 | 5068 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2269 | PRMAlarm_Hour_STK10 | 5070 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | STK 1.1
2270 | PRMAlarm_Hour_STK11 | 5072 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | STK 3.1
2271 | PRMAlarm_Hour_STK12 | 5074 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | STK 3.2
2272 | PRMAlarm_Hour_STK13 | 5076 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | STK 3.3
2273 | PRMAlarm_Hour_STK14 | 5078 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | STK 3.4
2274 | PRMAlarm_Hour_STK15 | 5080 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2275 | PRMAlarm_Hour_STK16 | 5082 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2276 | PRMAlarm_Hour_STK17 | 5084 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2277 | PRMAlarm_Hour_STK18 | 5086 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2278 | PRMAlarm_Hour_STK19 | 5088 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2279 | PRMAlarm_Hour_STK20 | 5090 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2280 | PRMAlarm_Hour_STK21 | 5092 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2281 | PRMAlarm_Hour_STK22 | 5094 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2282 | PRMAlarm_Hour_STK23 | 5096 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2283 | PRMAlarm_Hour_STK24 | 5098 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2284 | PRMAlarm_Hour_STK25 | 5100 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2285 | PRMAlarm_Hour_STK26 | 5102 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2286 | PRMAlarm_Hour_STK27 | 5104 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2287 | PRMAlarm_Hour_STK28 | 5106 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2288 | PRMAlarm_Hour_STK29 | 5108 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2289 | PRMAlarm_Hour_STK30 | 5110 | 0 | INT | PRM Alarm Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2290 | PRMDef_Hour_STK1 | 5112 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2291 | PRMDef_Hour_STK2 | 5114 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2292 | PRMDef_Hour_STK3 | 5116 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2293 | PRMDef_Hour_STK4 | 5118 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2294 | PRMDef_Hour_STK5 | 5120 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2295 | PRMDef_Hour_STK6 | 5122 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2296 | PRMDef_Hour_STK7 | 5124 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2297 | PRMDef_Hour_STK8 | 5126 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2298 | PRMDef_Hour_STK9 | 5128 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2299 | PRMDef_Hour_STK10 | 5130 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | STK 1.1
2300 | PRMDef_Hour_STK11 | 5132 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | STK 3.1
2301 | PRMDef_Hour_STK12 | 5134 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | STK 3.2
2302 | PRMDef_Hour_STK13 | 5136 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | STK 3.3
2303 | PRMDef_Hour_STK14 | 5138 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | STK 3.4
2304 | PRMDef_Hour_STK15 | 5140 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2305 | PRMDef_Hour_STK16 | 5142 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2306 | PRMDef_Hour_STK17 | 5144 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2307 | PRMDef_Hour_STK18 | 5146 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2308 | PRMDef_Hour_STK19 | 5148 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2309 | PRMDef_Hour_STK20 | 5150 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2310 | PRMDef_Hour_STK21 | 5152 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2311 | PRMDef_Hour_STK22 | 5154 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2312 | PRMDef_Hour_STK23 | 5156 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2313 | PRMDef_Hour_STK24 | 5158 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2314 | PRMDef_Hour_STK25 | 5160 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2315 | PRMDef_Hour_STK26 | 5162 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2316 | PRMDef_Hour_STK27 | 5164 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2317 | PRMDef_Hour_STK28 | 5166 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2318 | PRMDef_Hour_STK29 | 5168 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2319 | PRMDef_Hour_STK30 | 5170 | 0 | INT | PRM DEF Hour Stockage | BPCS/PSD | NO | PRM | Stockage | NO | NA | NO | NA
2320 | Admin Login | 5172 | 0 | BOOL | Niveau d'acces Admin Active | BPCS/PSD | NO | Status | IHM | YES | NA | YES | STATUS
2321 | HRSVariante_ResINT1 | 5176 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2322 | HRSVariante_ResINT2 | 5178 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2323 | HRSVariante_ResINT3 | 5180 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2324 | HRSVariante_ResINT4 | 5182 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2325 | HRSVariante_ResINT5 | 5184 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2326 | HRSVariante_ResINT6 | 5186 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2327 | HRSVariante_ResINT7 | 5188 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2328 | HRSVariante_ResINT8 | 5190 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2329 | HRSVariante_ResINT9 | 5192 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2330 | HRSVariante_ResINT10 | 5194 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2331 | HRSVariante_ResINT11 | 5196 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2332 | HRSVariante_ResINT12 | 5198 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2333 | HRSVariante_ResINT13 | 5200 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2334 | HRSVariante_ResINT14 | 5202 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2335 | HRSVariante_ResINT15 | 5204 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2336 | HRSVariante_ResINT16 | 5206 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2337 | HRSVariante_ResINT17 | 5208 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2338 | HRSVariante_ResINT18 | 5210 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2339 | HRSVariante_ResINT19 | 5212 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2340 | HRSVariante_ResINT20 | 5214 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2341 | HRSVariante_ResINT21 | 5216 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2342 | HRSVariante_ResINT22 | 5218 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2343 | HRSVariante_ResINT23 | 5220 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2344 | HRSVariante_ResINT24 | 5222 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2345 | HRSVariante_ResINT25 | 5224 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2346 | HRSVariante_ResINT26 | 5226 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2347 | HRSVariante_ResINT27 | 5228 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2348 | HRSVariante_ResINT28 | 5230 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2349 | HRSVariante_ResINT29 | 5232 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2350 | HRSVariante_ResINT30 | 5234 | 0 | INT |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2351 | HRSVariante_ResRL1 | 5236 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2352 | HRSVariante_ResRL2 | 5240 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2353 | HRSVariante_ResRL3 | 5244 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2354 | HRSVariante_ResRL4 | 5248 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2355 | HRSVariante_ResRL5 | 5252 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2356 | HRSVariante_ResRL6 | 5256 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2357 | HRSVariante_ResRL7 | 5260 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2358 | HRSVariante_ResRL8 | 5264 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2359 | HRSVariante_ResRL9 | 5268 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2360 | HRSVariante_ResRL10 | 5272 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2361 | HRSVariante_ResRL11 | 5276 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2362 | HRSVariante_ResRL12 | 5280 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2363 | HRSVariante_ResRL13 | 5284 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2364 | HRSVariante_ResRL14 | 5288 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2365 | HRSVariante_ResRL15 | 5292 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2366 | HRSVariante_ResRL16 | 5296 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2367 | HRSVariante_ResRL17 | 5300 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2368 | HRSVariante_ResRL18 | 5304 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2369 | HRSVariante_ResRL19 | 5308 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2370 | HRSVariante_ResRL20 | 5312 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2371 | HRSVariante_ResRL21 | 5316 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2372 | HRSVariante_ResRL22 | 5320 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2373 | HRSVariante_ResRL23 | 5324 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2374 | HRSVariante_ResRL24 | 5328 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2375 | HRSVariante_ResRL25 | 5332 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2376 | HRSVariante_ResRL26 | 5336 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2377 | HRSVariante_ResRL27 | 5340 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2378 | HRSVariante_ResRL28 | 5344 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2379 | HRSVariante_ResRL29 | 5348 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
2380 | HRSVariante_ResRL30 | 5352 | 0 | REAL |  | BPCS/PSD | NO | Reserve | NA | NO | NA | NO | NA
1 | "HDW_ESD_AIF_DG_H2_ATEX_Cont_DefVoi" | ns=3;s="DB_API_IHM_ETATS"."ETATS_1oo1_AIF"."AIF_DG_H2_ATEX_Cont"."Q_DEFAUT_VOIE" | NA |  | "" | SIS | NO | Reserve |  | NO | NA | NO | NA
2 | "HDW_ESD_AIF_DG_H2_ATEX_Vent_Cont_DefVoi" | ns=3;s="DB_API_IHM_ETATS"."ETATS_1oo1_AIF"."AIF_DG_H2_ATEX_Vent_Cont"."Q_DEFAUT_VOIE" | NA |  | "" | SIS | NO | Reserve |  | NO | NA | NO | NA
3 | "HDW_ESD_AIF_D1_DG_H2_dispenser_DefVoi" | ns=3;s="DB_API_IHM_ETATS"."ETATS_1oo1_AIF"."AIF_D1_DG_H2_dispenser"."Q_DEFAUT_VOIE" | NA |  | "" | SIS | NO | Reserve |  | NO | NA | NO | NA
4 | "HDW_ESD_AIF_D2_DG_H2_dispenser_DefVoi" | ns=3;s="DB_API_IHM_ETATS"."ETATS_1oo1_AIF"."AIF_D2_DG_H2_dispenser"."Q_DEFAUT_VOIE" | NA |  | "" | SIS | NO | Reserve |  | NO | NA | NO | NA
5 | "HDW_ESD_AIF_D2_DG_H2_platine_DefVoi" | ns=3;s="DB_API_IHM_ETATS"."ETATS_1oo1_AIF"."AIF_D2_DG_H2_platine"."Q_DEFAUT_VOIE" | NA |  | "" | SIS | NO | Reserve |  | NO | NA | NO | NA
6 | "HDW_ESD_AIF_D2_PT_Aval_DefVoi" | ns=3;s="DB_API_IHM_ETATS"."ETATS_1oo1_AIF"."AIF_D2_PT_Aval"."Q_DEFAUT_VOIE" | NA |  | "" | SIS | NO | Reserve |  | NO | NA | NO | NA
1 | "HSS_non_ATEX_Elec" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_HSS_non_ATEX_Elec" | NA | BOOL | HSS121 - Arrêt d'urgence armoire électrique - signal 1oo2 | ESD | YES | Status |  | YES | HSS 121 | NO | NA
2 | "DIF_CTRL_DIF_HSS_non_ATEX_Elec" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DIF_HSS_non_ATEX_Elec" | NA | BOOL | HSS121 - Arrêt d'urgence armoire électrique - signal 1oo2 - Value Status | ESD | YES | Status |  | YES | HSS 121 | NO | NA
3 | "DIF_HSS_non_ATEX_Roof" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_HSS_non_ATEX_Roof" | NA | BOOL | HSS122 - Arrêt d'urgence étage container - signal 1oo2 | ESD | YES | Status |  | YES | HSS 122 | NO | NA
4 | "DIF_CTRL_DIF_HSS_non_ATEX_Roof" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DIF_HSS_non_ATEX_Roof" | NA | BOOL | HSS122 - Arrêt d'urgence étage container - signal 1oo2 - Value Status | ESD | YES | Status |  | YES | HSS 122 | NO | NA
5 | "DIF_ESD_Max" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_ESD_Max" | NA | BOOL | Arrêt d'urgence en provenance de Maximator - signal 1oo2 | ESD | YES | Status |  | YES |  | NO | NA
6 | "DIF_CTRL_DIF_ESD_Max" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DIF_ESD_Max" | NA | BOOL | Arrêt d'urgence en provenance de Maximator - signal 1oo2 - Value Status | ESD | YES | Status |  | YES |  | NO | NA
7 | "DIF_HSS_CLIENT" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_HSS_CLIENT" | NA | BOOL | HSS120 - Arrêt d'urgence client - signal 1oo2 | ESD | YES | Status |  | YES | HSS 120 | NO | NA
8 | "DIF_CTRL_DIF_HSS_CLIENT" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DIF_HSS_CLIENT" | NA | BOOL | HSS120 - Arrêt d'urgence client - signal 1oo2 - Value Status | ESD | YES | Status |  | YES | HSS 120 | NO | NA
9 | "DIF_D1_HSS" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_D1_HSS" | NA | BOOL | HSS82 - Arrêt d'urgence dispenser LDV - signal 1oo2 | ESD | YES | Status |  | YES |  | NO | NA
10 | "DIF_CTRL_DIF_D1_HSS" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DIF_D1_HSS" | NA | BOOL | HSS82 - Arrêt d'urgence dispenser LDV - signal 1oo2 - Value Status | ESD | YES | Status |  | YES |  | NO | NA
11 | "DIF_HSS_STK" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_HSS_STK" | NA | BOOL | HSS50 - Arrêt d'urgence platine gaz - signal 1oo2 | ESD | YES | Status |  | YES |  | NO | NA
12 | "DIF_CTRL_DIF_HSS_STK" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DIF_HSS_STK" | NA | BOOL | HSS50 - Arrêt d'urgence platine gaz - signal 1oo2 - Value Status | ESD | YES | Status |  | YES |  | NO | NA
13 | "DIF_HSS_Fence_1" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_HSS_Fence_1" | NA | BOOL | Arrêt d'urgence client FENCE 1 - signal 1oo2 | ESD | YES | Status |  | YES |  | NO | NA
14 | "DIF_CTRL_DIF_HSS_Fence_1" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DIF_HSS_Fence_1" | NA | BOOL | Arrêt d'urgence client FENCE 1 - signal 1oo2 - Value Status | ESD | YES | Status |  | YES |  | NO | NA
15 | "DIF_HSS_Fence_2" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_HSS_Fence_2" | NA | BOOL | Arrêt d'urgence client FENCE 2 - signal 1oo2 | ESD | YES | Status |  | YES |  | NO | NA
16 | "DIF_CTRL_DIF_HSS_Fence_2" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DIF_HSS_Fence_2" | NA | BOOL | Arrêt d'urgence client FENCE 2 - signal 1oo2 - Value Status | ESD | YES | Status |  | YES |  | NO | NA
17 | "DIF_HSS_Fence_3" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_HSS_Fence_3" | NA | BOOL | Arrêt d'urgence client FENCE 3 - signal 1oo2 | ESD | YES | Status |  | YES |  | NO | NA
18 | "DIF_CTRL_DIF_HSS_Fence_3" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DIF_HSS_Fence_3" | NA | BOOL | Arrêt d'urgence client FENCE 3 - signal 1oo2 - Value Status | ESD | YES | Status |  | YES |  | NO | NA
19 | "DIF_HSS_Fence_4" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_HSS_Fence_4" | NA | BOOL | Arrêt d'urgence client FENCE 4 - signal 1oo2 | ESD | YES | Status |  | YES |  | NO | NA
20 | "DIF_CTRL_DIF_HSS_Fence_4" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DIF_HSS_Fence_4" | NA | BOOL | Arrêt d'urgence client FENCE 4 - signal 1oo2 - Value Status | ESD | YES | Status |  | YES |  | NO | NA
21 | "DIF_RMP_station_1" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_RMP_station_1" | NA | BOOL | Retour mise en puissance station (11KM01) - contact NF | ESD | YES | Status |  | YES |  | NO | NA
22 | "DIF_CTRL_DIF_RMP_station_1" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DIF_RMP_station_1" | NA | BOOL | Retour mise en puissance station (11KM01) - Value Status | ESD | YES | Status |  | YES |  | NO | NA
23 | "DIF_BP_rearm_ESD" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_BP_rearm_ESD" | NA | BOOL | BP réarmement ESD (contact NO) | ESD | YES | Status |  | YES |  | NO | NA
24 | "DIF_CTRL_DIF_BP_rearm_ESD" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DIF_BP_rearm_ESD" | NA | BOOL | BP réarmement ESD - Value Status | ESD | YES | Status |  | YES |  | NO | NA
25 | "DIF_HSS_LP" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_HSS_LP" | NA | BOOL | HSS52 - Arrêt d'urgence Onsite LP storage AREA - signal 1oo2 | ESD | YES | Status |  | YES |  | NO | NA
26 | "DIF_CTRL_DIF_HSS_LP" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DIF_HSS_LP" | NA | BOOL | HSS52 - Arrêt d'urgence Onsite LP storage AREA - signal 1oo2 - Value Status | ESD | YES | Status |  | YES |  | NO | NA
27 | "DIF_HSS_Trailer" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_HSS_Trailer" | NA | BOOL | HSS53 - Arrêt d'urgence tube trailer off-loading area - signal 1oo2 | ESD | YES | Status |  | YES |  | NO | NA
28 | "DIF_CTRL_DIF_HSS_Trailer" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DIF_HSS_Trailer" | NA | BOOL | HSS53 - Arrêt d'urgence tube trailer off-loading area - signal 1oo2 - Value Status | ESD | YES | Status |  | YES |  | NO | NA
29 | "DIF_RMP_station_2" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_RMP_station_2" | NA | BOOL | Retour mise en puissance station (11KM02) - contact NF | ESD | YES | Status |  | YES |  | NO | NA
30 | "DIF_CTRL_DIF_RMP_station_2" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DIF_RMP_station_2" | NA | BOOL | Retour mise en puissance station (11KM02) - Value Status | ESD | YES | Status |  | YES |  | NO | NA
31 | "DIF_D1_VFC_isolement_PSL_air" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_D1_VFC_isolement_PSL_air" | NA | BOOL | PSL8.201 - presence air VFC8.201 vanne isolement distrib - signal 1oo2 | ESD | YES | Status |  | YES |  | NO | NA
32 | "DIF_CTRL_DIF_D1_VFC_isolement_PSL_air" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DIF_D1_VFC_isolement_PSL_air" | NA | BOOL | PSL8.201 - presence air VFC8.201 vanne isolement distrib - signal 1oo2 - Value Status | ESD | YES | Status |  | YES |  | NO | NA
33 | "DIF_D1_VFO_Purge_Av_air" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_D1_VFO_Purge_Av_air" | NA | BOOL | PSL8.202 - presence air VFO8.202 vanne purge aval distrib - signal 1oo2 | ESD | YES | Status |  | YES |  | NO | NA
34 | "DIF_CTRL_DIF_D1_VFO_Purge_Av_air" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DIF_D1_VFO_Purge_Av_air" | NA | BOOL | PSL8.202 - presence air VFO8.202 vanne purge aval distrib - signal 1oo2 - Value Status | ESD | YES | Status |  | YES |  | NO | NA
35 | "DIF_CTRL_AIF_TT_amb_LP" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_AIF_TT_amb_LP" | NA | BOOL | TT52 - Température Ambiance Onsite LP storage area - Value Status | ESD | YES | Status |  | YES |  | NO | NA
36 | "DIF_CTRL_AIF_TT_amb_Trailer" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_AIF_TT_amb_Trailer" | NA | BOOL | TT53 - Température Ambiance tube trailer off-loading area - Value Status | ESD | YES | Status |  | YES |  | NO | NA
37 | "DIF_CTRL_AIF_D1_DG_H2_dispenser" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_AIF_D1_DG_H2_dispenser" | NA | BOOL | DG82 détecteur de fuite H2 zone dispenser LDV - Value Status | ESD | YES | Status |  | YES |  | NO | NA
38 | "DIF_CTRL_AIF_D1_PT_Aval_Secu_1_b" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_AIF_D1_PT_Aval_Secu_1_b" | NA | BOOL | PT8.201b - Transmetteur de pression H2 ligne LDV1 - Value Status | ESD | YES | Status |  | YES |  | NO | NA
39 | "DIF_CTRL_AIF_D1_PT_Aval_Secu_2_b" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_AIF_D1_PT_Aval_Secu_2_b" | NA | BOOL | PT8.202b - Transmetteur de pression H2 ligne LDV1 - Value Status | ESD | YES | Status |  | YES |  | NO | NA
40 | "DIF_CTRL_AIF_TT_amb_platine_dist" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_AIF_TT_amb_platine_dist" | NA | BOOL | TT50 - Température Ambiance Platine déportée - Value Status | ESD | YES | Status |  | YES |  | NO | NA
41 | "DIF_CTRL_AIF_TT_amb_stockages" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_AIF_TT_amb_stockages" | NA | BOOL | TT51 - Température Ambiance zone de stockages - Value Status | ESD | YES | Status |  | YES |  | NO | NA
42 | "DIF_CTRL_AIF_TT_amb_maxpower" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_AIF_TT_amb_maxpower" | NA | BOOL | TT123 - Température Ambiance Max Power - Value Status | ESD | YES | Status |  | YES |  | NO | NA
43 | "DIF_CTRL_AIF_D1_TT_amb_dispenser" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_AIF_D1_TT_amb_dispenser" | NA | BOOL | TT82 - Température Ambiance Dispenser LDV1 - Value Status | ESD | YES | Status |  | YES |  | NO | NA
44 | "DIF_CTRL_AIF_TT_Amb_ATEX_Cont" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_AIF_TT_Amb_ATEX_Cont" | NA | BOOL | TT61 - Température Ambiance extérieure compression - Value Status | ESD | YES | Status |  | YES |  | NO | NA
45 | "DIF_CTRL_AIF_TT_amb_non_ATEX_Cont" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_AIF_TT_amb_non_ATEX_Cont" | NA | BOOL | TT121 - Température Ambiance extérieure zone utilités - Value Status | ESD | YES | Status |  | YES |  | NO | NA
46 | "DIF_CTRL_AIF_TT_amb_ext_container" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_AIF_TT_amb_ext_container" | NA | BOOL | TT122 - Température Ambiance extérieure du conteneur - Value Status | ESD | YES | Status |  | YES |  | NO | NA
47 | "DIF_CTRL_AIF_TT_amb_armoire" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_AIF_TT_amb_armoire" | NA | BOOL | TT124 - Température Ambiance intérieure armoire HRS - Value Status | ESD | YES | Status |  | YES |  | NO | NA
48 | "DIF_CTRL_DOF_MEP_station_1" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DOF_MEP_station_1" | NA | BOOL | Mise en puissance station (11KM01) - Value Status | ESD | YES | Status |  | YES |  | NO | NA
49 | "DIF_CTRL_DOF_MEP_station_2" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DOF_MEP_station_2" | NA | BOOL | Mise en puissance station (11KM02) - Value Status | ESD | YES | Status |  | YES |  | NO | NA
50 | "DIF_CTRL_DOF_YSI12_82_Rd" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DOF_YSI12_82_Rd" | NA | BOOL | Verrines rouges Etat défaut station et dispenser - Value Status | ESD | YES | Status |  | YES |  | NO | NA
51 | "DIF_CTRL_DOF_ARRET_CUST" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DOF_ARRET_CUST" | NA | BOOL | Signal arret McPhy vers client - bornier client - Value Status | ESD | YES | Status |  | YES |  | NO | NA
52 | "DIF_CTRL_DOF_Voyant_rearm_ESD" | ns=3;s="DB_SIMUL_DIF"."DIF"."DIF_CTRL_DOF_Voyant_rearm_ESD" | NA | BOOL | Voyant réarment ESD - Value Status | ESD | YES | Status |  | YES |  | NO | NA
53 | "AIF_TT_amb_LP" | ns=3;s="DB_SIMUL_AIF"."AIF"."AIF_TT_amb_LP" | NA | INT | TT52 - Température Ambiance Onsite LP storage area (en points) | ESD | YES | Measure |  | YES |  | NO | NA
54 | "AIF_TT_amb_Trailer" | ns=3;s="DB_SIMUL_AIF"."AIF"."AIF_TT_amb_Trailer" | NA | INT | TT53 - Température Ambiance tube trailer off-loading area (en points) | ESD | YES | Measure |  | YES |  | NO | NA
55 | "AIF_D1_DG_H2_dispenser" | ns=3;s="DB_SIMUL_AIF"."AIF"."AIF_D1_DG_H2_dispenser" | NA | INT | DG82 - détecteur de fuite H2 zone dispenser LDV (en points) | ESD | YES | Measure |  | YES |  | NO | NA
56 | "AIF_D1_PT_Aval_Secu_1_b" | ns=3;s="DB_SIMUL_AIF"."AIF"."AIF_D1_PT_Aval_Secu_1_b" | NA | INT | PT8.201b - Transmetteur de pression H2 ligne LDV (en points) | ESD | YES | Measure |  | YES |  | NO | NA
57 | "AIF_D1_PT_Aval_Secu_2_b" | ns=3;s="DB_SIMUL_AIF"."AIF"."AIF_D1_PT_Aval_Secu_2_b" | NA | INT | PT8.202b - Transmetteur de pression H2 ligne LDV (en points) | ESD | YES | Measure |  | YES |  | NO | NA
58 | "AIF_TT_amb_platine_dist" | ns=3;s="DB_SIMUL_AIF"."AIF"."AIF_TT_amb_platine_dist" | NA | INT | TT50 - Température Ambiance Platine déportée (en points) | ESD | YES | Measure |  | YES |  | NO | NA
59 | "AIF_TT_amb_stockages" | ns=3;s="DB_SIMUL_AIF"."AIF"."AIF_TT_amb_stockages" | NA | INT | TT51 - Température Ambiance zone de stockages (en points) | ESD | YES | Measure |  | YES |  | NO | NA
60 | "AIF_TT_amb_maxpower" | ns=3;s="DB_SIMUL_AIF"."AIF"."AIF_TT_amb_maxpower" | NA | INT | TT123 - Température Ambiance Max Power (en points) | ESD | YES | Measure |  | YES |  | NO | NA
61 | "AIF_D1_TT_amb_dispenser" | ns=3;s="DB_SIMUL_AIF"."AIF"."AIF_D1_TT_amb_dispenser" | NA | INT | TT82 - Température Ambiance Dispenser LDV1 (en points) | ESD | YES | Measure |  | YES |  | NO | NA
62 | "AIF_TT_Amb_ATEX_Cont" | ns=3;s="DB_SIMUL_AIF"."AIF"."AIF_TT_Amb_ATEX_Cont" | NA | INT | TT61 - Température Ambiance extérieure compression (en points) | ESD | YES | Measure |  | YES |  | NO | NA
63 | "AIF_TT_amb_non_ATEX_Cont" | ns=3;s="DB_SIMUL_AIF"."AIF"."AIF_TT_amb_non_ATEX_Cont" | NA | INT | TT121 - Température Ambiance extérieure zone utilités (en points) | ESD | YES | Measure |  | YES |  | NO | NA
64 | "AIF_TT_amb_ext_container" | ns=3;s="DB_SIMUL_AIF"."AIF"."AIF_TT_amb_ext_container" | NA | INT | TT122 - Température Ambiance extérieure du conteneur (en points) | ESD | YES | Measure |  | YES |  | NO | NA
65 | "AIF_TT_amb_armoire" | ns=3;s="DB_SIMUL_AIF"."AIF"."AIF_TT_amb_armoire" | NA | INT | TT124 - Température Ambiance intérieure armoire HRS (en points) | ESD | YES | Measure |  | YES |  | NO | NA